## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
172267 | A | CEILING SUSPENDENT HANDLING UNITS Supply, Installation, Testing and Commissioning of Double Skin Ceiling Suspendent Air Handling Direct Driven Unit, made out of modular panel of thickness 43 + - 2 mm thick, with thermal break profile, with following section CSU frame work shall be Anodized Aluminum Section with thermal break profile internal coving. Mixing box with FAD and RAD with AL construction. Filter section with Pre-filter (G4) + Fine-filter (F5) (Combination Filter) Cooling Coil section with 4 row deep CHW type cooling coil . Fan Section with DIDW type Fan.centrifugal forward curved fan.ceiling suspendent direct driven. Supply air damper in AL construction. |  | 0.00 | 0.00 |  | 0
172268 | 1.1 | CSAHU No 01 @30mmWC - 2400CFM | NOS | 0.00 | 1.00 |  | 0
172269 | 2 | Kitchen Scrubber (Dry Type)-With Fan Section (Floor Mounted) Make Trion Rydair |  | 0.00 | 0.00 |  | 0
172270 |  | 4500 CFM DIDW Blower Capacity at 110 MM SP | Nos. | 0.00 | 1.00 |  | 0
172271 | 2.1 | Supply, Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14 deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air Operating Voltage 220V, 50 HzIonizing Voltage 12.5 to 13 KVDCCollector Cell Voltage 6 to 6.5 KVDCPower Consumption Not more than 50W per cell.with Variable frequency Drive (VFD) |  | 0.00 | 0.00 |  | 0
172272 | 3 | FACTORY FABRICATED DOUBLE SKIN AIR WASHER | Nos | 0.00 | 1.00 |  | 0
172273 |  | Supply, installation, testing and commissioning of factory fabricated Double Skinned Air-washer unit floor mounted type fabricated out of extruded aluminium section with 0.6mm pre-plasticized pre-coated Galvanised steel sheet outside 0.6 mm plain Galvanised steel sheet inside with blower, blower section and blower motor TEFC (IE-3) type suitable for operation on 415 volts ± 10%, 50 Hz ± 5% AC supply, belt drive package, wet section tank shall be made of 18 G stainless steel. The Air-washer shall be complete with fill of depth 200 mm face velocity across the fill shall be limited to 152 MPM. The Air-washer shall have an efficiency of 90% shall be complete with water circulation pump -2 Nos.(1W+1S), GI B Class interconnecting piping,Aluminum viscous filters. makeup, quickfill and drain connections, Butterfly Gate valves for Pumps, make up, drain quickfill connections of Sump, 2 Nos. pumps of suitable capacity (1W +1 S), Y strainers and necessary fittings etc. Suitable PCC RCC foundation with plaster, Antivibration arrangement of cushy foot mountings etc.in all respect shall be in contractor s scope. The Air-washer shall have an efficiency of 90% shall be complete with water circulation pump GI B Class interconnecting piping valves Aluminum viscous filters, fire retardent double canvass connection etc. The airwasher panels shall be insulated with 23mm thick 36 Kg m³ density PU foam. The Airwasher shall conform to specication given in the tender shall be of following capacity. Motor Kw is indicative only, actual as per requirement to be included during installation. Duty Kitchen Fresh Air Air Qty 3600 CFM Static Pressure 90 mm wg |  | 0.00 | 0.00 |  | 0
172274 | 4 | FRESH AIR UNITSSupply, Installation, Testing and Commissioning of Double Skin Fresh Air Unit, made out of modular panel of thickness 25 mm thick, with thermal break profile, with following section F.A.H frame work shall be Anodized Aluminum Section with thermal break profile internal coving.Fan Section with DIDW type Fan.centrifugal forward curved fan.ceiling suspendent direct driven.Supply air damper in AL construction. |  | 0.00 | 0.00 |  | 0
172275 | 1.1 | F.A.U No 01 @30mmWC - 1200 CFM | NOS | 0.00 | 1.00 |  | 0
172276 | 1.2 | Drain Piping Supply, installation, testing and commissioning of PVC drain piping complete with fittings, U traps, supports for below pipe size. 32 NB 25 NB | Rmtr. | 0.00 | 20.00 |  | 0
172277 |  | Note - Piping quantity will vary as per actual site condition. |  | 0.00 | 0.00 |  | 0
172278 |  | General Guidelines Ducting 1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C for air conditioning ducting. 2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg m33) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil grease cleaning purpose.5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia As per duct size.8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident. 10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.11) Trap door with proper access to be provided for filter and copper coil cleaning.12) Kitchen ventilation shall comply to NFPA 96 guideline.Chilled Water Piping - 1. Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc.3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.6. For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. 7. Attached CHW P ID drawing sketch to be followed during onsite work. |  | 0.00 | 0.00 |  | 0