## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
176742 | 1 | PANELS DBsSupply and Installation of main LT panel,genarally conforming to IS 8623 IS-13947 IEC-439 front operated, dead back floor mounted , totally enclosed, compartmentalised, vermin proof,indoor, non-drawout type,power panel, fabricated out of 2 1.6mm thick CRCA sheets, fully powder coated after seven tank treatment, having gasketed hinged cover on each cubicle with insulated door knob, incorporating horizontal and vertical copper busbars complete with all internal wiring, danger sign board, earth-bus and lugs, cable chamber, busbar chamber,aluminium anodized name plates etc.as required, including 2 nos. of 6 dia instrument cooling fan with switch and ventilation louvres with wire mesh,housing below mentioned switchgears meters. 9W fitting with CFL lamp, switch shall be provided in each vertical section, (Panel should conform to Form- 3b of IEC- 439) (GA drawing of the panel to be got approved from the Consultant before taking up fabrication and all panels to be factory inspected before despatch) Notes 1. All MCCBs shall have rotary handle 2. All MCCBs shall have phase spreader assembly onboth Line Load ends. 3. All MCCB shall have Minimum Ics=Icu4. Incomer shall have auxilliary ON OFF TRIP status contacts and the same shall be wired upelectronic trip setting to Metering Compartment)5. The panel shall conform to Form-3b as per IEC-4396. All MCCB to be of Schneider ABB make7. All MCCB to be current limiting type, LSIG 8. Incomer MCCB to be shunt trip facility7. With DOL Starter 2.2KW 1.5KW for air washer exhaust fan8. With VFD for 2.2KW 1.5KW for air washer exhaust fan make Selec9.Please provide CO2,FM200 HFC-227ea gas based automatic tube detection suppression system needs to be installed in Electrical Panel Refer SLD |  | 0.00 | 0.00 |  | 0
176743 | 1.1.1 | MAIN PANEL | Set | 0.00 | 1.00 |  | 250000
176744 | 1.2 | Suply and installation of Four -Tier, Multi-Way, TPN, Distribution Board for Lighting Power distribution, surface mounted on wall, sheet metal fabricated,powder coated, having dust-proof and vermin proof, gasketed and hinged acrylic door with all internals such as DIN rails, neutral-link, interconnected wiring complete with earthing lugs housing switchgears (IP-43 with Metal Door) Refer SLD DB Schedule (Make Legrand-Ekinoxe Schneider) |  | 0.00 | 0.00 |  | 0
176745 | 1.2.1 | KITCHEN DB 1 (KPDB-12WAY TPN) | Set | 0.00 | 1.00 |  | 35000
176746 | 1.2.2 | KITCHEN DB 2 (BARDB-8WAY TPN) | Set | 0.00 | 1.00 |  | 33000
176747 | 1.2.3 | LPDB 1 (12WAY TPN) | Set | 0.00 | 1.00 |  | 35000
176748 | 1.2.4 | UPS OUTPUT | Set | 0.00 | 1.00 |  | 13000
176749 | 1.2.4 | UPSDB (16WAY SPN) | Set | 0.00 | 1.00 |  | 13500
176750 | 1.5 | S I of 16A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 0.00 | 8.00 |  | 4500
176751 | 2.0 | CABLES |  | 0.00 | 0.00 |  | 0
176752 | 2.1 | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts laid in ground laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications. |  | 0.00 | 0.00 |  | 0
176753 | 2.1.5 | 3.5C x 35 Sq.mm. AL Cable | R.M | 0.00 | 80.00 |  | 550
176754 | 2.1.7 | 4C x 16 Sq.mm. CU Cable - KPDB1 KPDB2, ELECTRIC HOT PLATE | R.M | 0.00 | 80.00 |  | 850
176755 | 2.1.9 | 4C x 6 Sq.mm. CU Cable - KITCHEN EXHUAST FRESH AIR | R.M | 0.00 | 20.00 |  | 450
176756 | 2.1.10 | 4C x 4 Sq.mm. CU Cable - AHU | R.M | 0.00 | 20.00 |  | 350
176757 | 2.1.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | R.M | 0.00 | 50.00 |  | 450
176758 | 2.1.18 | 3C X 1.5sq.mm CU PVC Cable | R.M | 0.00 | 20.00 |  | 250
176759 | 2.1.21 | 2C X 2.5sq.mm CU Cable | R.M | 0.00 | 25.00 |  | 250
176760 | 2.1.22 | 5C X 2.5sq.mm CU Cable - LCS | R.M | 0.00 | 25.00 |  | 350
176761 | 2.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
176762 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
176763 | 2.2.5 | 3.5C x 35 Sq.mm. AL Cable | Nos. | 0.00 | 2.00 |  | 1200
176764 | 2.2.7 | 4C x 16 Sq.mm. CU Cable - KPDB1 KPDB2, ELECTRIC HOT PLATE | Nos. | 0.00 | 8.00 |  | 1000
176765 | 2.2.9 | 4C x 6 Sq.mm. CU Cable - KITCHEN EXHUAST FRESH AIR | Nos. | 0.00 | 2.00 |  | 500
176766 | 2.2.10 | 4C x 4 Sq.mm. CU Cable - AHU | Nos. | 0.00 | 6.00 |  | 500
176767 | 2.2.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | Nos. | 0.00 | 7.00 |  | 500
176768 | 2.2.18 | 3C X 1.5sq.mm CU PVC Cable | Nos. | 0.00 | 2.00 |  | 500
176769 | 2.2.21 | 2C X 2.5sq.mm CU Cable | Nos. | 0.00 | 8.00 |  | 500
176770 | 2.2.22 | 5C X 2.5sq.mm CU Cable - LCS | Nos. | 0.00 | 8.00 |  | 500
176771 | 3.0 | POINT WIRING LIGHT POINTSub mains Pre-Primary wiring i.e. from DB to room switch board shall be carried out for Pre-primary point using 2.5 sqmm copper stranded. All lighting fixture, wiring shall be carried out for primary point using 2.5 sqmm copper stranded for secondary wiring 1.5sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduits (including flexible conduits for drops to light fittings) . Individual junction inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12-8 points 800 watts as per following configuration (LDBs located at two locations as shown) (The Switch Socket cost shall be paid separately.)From distribution board to switch board will be termed as Pre-primary point, average wiring length for Pre-primary point to be considered as 15 metres. From switch board to first light fitting and switch board to switch board will be termed as primary point, average wiring length for primary point to be considered as 6 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 4 metres. Light point wiring shall be included submains wiring from D.B. to room switch board. Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
176772 |  | Total points | Nos | 0.00 | 40.00 |  | 2300
176773 | 3.4 | Power Point (Kitchen FOH)Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 4 sqmm copper stranded. Also used 3R x 2.5sqmm copper stranded. Secondary wiring 4 sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduits . Individual junction inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 22 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 1 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point. Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
176774 | 3.4.1 | total points | Nos | 0.00 | 36.00 |  | 4500
176775 | 3.7 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular shuttered type switch socket outlets with modular front plate, on Suitable MS box, G.I. back box and all required accessories etc. Supply Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw wall plugs and other necessary hardware, marking identification numbers of circuits interconnections of the switch sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND |  | 0.00 | 0.00 |  | 0
176776 | 3.7.1 | 6A SWITCH SOCKET(UTILITY POINT) | Nos. | 0.00 | 5.00 |  | 600
176777 | 3.7.2 | POS COUNTER | Nos. | 0.00 | 1.00 |  | 1000
176778 | 3.7.4 | 5 15A POWER PLUG POINT(MODULAR SWITCH SOCKET) | Nos. | 0.00 | 10.00 |  | 7000
176779 | 3.7.5 | 20 32A METAL CLAD WITH 20A SP MCB PLUG TOP | Nos. | 0.00 | 4.00 |  | 3500
176780 | 3.7.22 | 5 Pin Industrial 16A Socket (3 PHASE) | Nos. | 0.00 | 4.00 |  | 6000
176781 | 3.7.24 | DATA POINT | Nos. | 0.00 | 1.00 |  | 800
176782 | 4.0 | RACEWAYS, CABLE TRAYS JUNCTION BOX |  | 0.00 | 0.00 |  | 0
176783 | 4.4 | S I of 1 Run x 25mm dia, GI Conduit in Floor. | Mtr | 0.00 | 6.00 |  | 190
176784 | 5.0 | LIGHT FIXTURES INSTALLATION |  | 0.00 | 0.00 |  | 0
176785 | 5.1 | Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect consultant at site. |  | 0.00 | 0.00 |  | 0
176786 | 5.1.1 | CEILING PANEL LIGHT | Nos | 0.00 | 20.00 |  | 800
176787 | 5.1.2 | HANGING LIGHT | Nos | 0.00 | 5.00 |  | 300
176788 | 5.1.3 | CYLINDRICAL LIGHT | Nos | 0.00 | 20.00 |  | 300
176789 | 6.0 | EARTHING |  | 0.00 | 0.00 |  | 0
176790 | 6.1 | S I of earth pit comprising of specially designed SEE Ashlok brand Earth Electrode system 3.00 meter long including necessary materials like side fill compound etc. as required with standard brick masonary chamber with hinged cover and watering arrangement model SEE-60 C with SFC-20 Equivalent ASHLOK MODEL T39 HD (50MM DIA. 3 MTR) | Nos | 0.00 | 2.00 |  | 8000
176791 | 6.3 | 8 SWG GI bare wire | Mtr | 0.00 | 50.00 |  | 40
176792 | 6.4 | 8 SWG CU bare wire | Mtr | 0.00 | 20.00 |  | 150
176793 | 6.6 | 25mm x 6mm thick GI strip welded painted green | Mtr | 0.00 | 40.00 |  | 250
176794 | 6.7 | S I of isolated dedicated earthing grounding system for computers etc.using insulated green-yellow copper earthing wire laid fixed bare on wall ceiling from separately made earth pit to the equipment in following sizes The rate shall include termination also. |  | 0.00 | 0.00 |  | 0
176795 | 6.7.1 | 6 Sqmm copper, yellow-green green insulation | Mtr | 0.00 | 10.00 |  | 120
176796 | 6.8 | S I of Main bus for isolated earth comprising of 300mm x 25 mm x 3mm thick Tinned copper bar fixed on insulated support and having 10 nos of holes and nut bolts studs for clamping the earth leads,all contained in MS PVC box and having transparent acrylic cover as approved by the consultant | Nos | 0.00 | 1.00 |  | 2500
176797 | 7 | Miscellaneous Item |  | 0.00 | 0.00 |  | 0
176798 | 7.1 | Supply Install. Of RG 6 TV Cable in 25mm PVCConduit | Mtr. | 0.00 | 45.00 |  | 80
176799 | 7.2 | Supply Laying of RG11 use for Main Cable TV | Mtr. | 0.00 | 45.00 |  | 80
176800 | 7.3 | Install. Of Digital Screen - Only Installation | Nos. | 0.00 | 7.00 |  | 500
176801 | 8 | DATA DISTRIBUTION |  | 0.00 | 0.00 |  | 0
176802 |  | Supply, Installation, termination testing of data system |  | 0.00 | 0.00 |  | 0
176803 | 8.2 | SMART GIGABIT SWITCH 16 PORTS | Nos. | 0.00 | 1.00 |  | 10000
176804 | 8.3 | Loaded PATCH PANEL for 16Port | Nos. | 0.00 | 1.00 |  | 8000
176805 | 8.4 | LIU switch with Accessories. (Optional if Fibre Optic Cable terminated) | Job | 0.00 | 1.00 |  | 7000
176806 | 8.5 | Supply Installation of I O DATA Outlet (RJ-45) | Nos. | 0.00 | 2.00 |  | 700
176807 | 8.8 | CABLES |  | 0.00 | 0.00 |  | 0
176808 | 8.8.3 | Supply providing of CAT 6 UTP cables in the laid raceways Conduits including terminations | Mtr. | 0.00 | 16.80 |  | 80
176809 | 8.8.4 | Patch cord (2 mtr-user end) | Each | 0.00 | 2.00 |  | 300
176810 | 8.9 | Supply, Installation, Testing Commissioning of Velcro Ties ( 22 Mtrs = 1 Roll) | Roll | 0.00 | 1.00 |  | 500
176811 | 8.10. | Supply, Installation, Testing Commissioning of Cable Ties 200mm ( 100 Nos. Pkt) | Pkt. | 0.00 | 1.00 |  | 500
176812 | 8.11 | Project Management including Freight Forwarding, Cable Bunching, Printed Numbering, tube type Ferruling both sides, Face plate, Patch panel patch cords both sides, Documentation etc.. | Job | 0.00 | 1.00 |  | 20000
176813 | 8.13 | Supply installation of GI Conduits with junction boxes, reducer etc. complete concealed surface mounting as required. |  | 0.00 | 0.00 |  | 0
176814 | 9.0 | SUPPLY INSTALLATION OF SAFETY ITEMS |  | 0.00 | 0.00 |  | 0
176815 | 9.3 | Caution boards (415V) of std. Size | Nos | 0.00 | 1.00 |  | 300
176816 | 9.4 | Rubber mat at panel room 12mm thk. 1mtr. Wide | Mtrs | 0.00 | 1.00 |  | 500
176817 | 9.5 | Shock treatment chart as per electricity board | Nos | 0.00 | 1.00 |  | 300
176818 | 9.8 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical ELV Services executed at site. | Part of Tender | 0.00 | 0.00 |  | 0
176819 | 10.0 | UPS INVERTER System |  | 0.00 | 0.00 |  | 0
176820 | 10.1 | Supply, Installation, testing and commissioning of 3 KVA UPS System Single Phase I C Single Phase O G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings the specifications. Make Emerson APC Consul Neowatt Vivtar Electronics | set | 0.00 | 1.00 |  | 120000
176821 | 11.0 | CCTV |  | 0.00 | 0.00 |  | 0
176822 | 11.10 | Supply Installation of 3+1 Cable for Camera with GU Couduit | Mtr. | 0.00 | 90.00 |  | 250
176823 |  | General guideline for onsite electrical works 1. DB have per phase RCBO protection.2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.3. All equipment’s above 1 KW shall be provided with ELCB shall run operated through industrial type switch socket only.4. Only GI conduit will be used.5. Equipment protection devices and appropriate earthing as per approved load to be provided.6. All DB and panel have dual earthing connection.7. All internal wires cables shall be FRLSHRLSZH.8. Main distribution board will not be fixed on wooden material.9. IT , Data and low voltage wires shall be drawn In Separate10. Switch Sockets outlets will not be over loaded with multiple connection conduit and not with electrical11. All lights shall be LED.12. Provision of Emergency light should be there.13. No combustive material are to be store under closed the electrical switch boarddistribution board meter etc.14. The concessioner should install suitable type rated fire extinguisher near electrical panel.15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.17. Final approved Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.18. Load balancing to be done.19. Power connection for Existing BTU meter Water meter to be provided from concessionaire DB.22. Before installation, material inspection to be done.23. Test certificate for installed electrical material to be submitted to DIAL . 24. If any changes due to site constraint, prior intimation to be provided to DIAL. Post approval only SLD to revised.25.all SP MCB as ‘C’ characteristic.In case, Incomer rating equal to or more than 200Amps Automatic Tube Detection and Suppression System to be doneCO2,FM200HFC-227ea gas based automatic tube detection suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.Drawing needs to be submitted for prior approval.System sizing design calculations also need to be incorporated in drawing.20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.21. Panel GA drawing to be share with DIAL for approval. |  | 0.00 | 0.00 |  | 0