## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
104178 | A | METER METER PANEL |  | 0.00 | 0.00 |  | 0
104179 | A.1 | Supply, Installation, Testing Commissioning of Energy Meter Meter Panel (Prepaid Type) complete with Enclosure (If required as per site condition Airport TDM). Make Brand selection as per Airport TDM listed. |  | 0.00 | 0.00 |  | 0
104180 | A.1.1 | 125A 5A ENERGY METER (CT TYPE) | Nos. | 0.00 | 1.00 |  | 0
104181 | B | LV CABLING |  | 0.00 | 0.00 |  | 0
104182 | B.1 | Supply, Installation, Testing Commissioning of Fire Rated LSH LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground on Cable Tray in Pipe on Wall Trench as required. For cables laid on Cable Tray in Pipe on Wall Trench - the rate shall include necessary supporting clamping arrangements. |  | 0.00 | 0.00 |  | 0
104183 | B.1.2 | 4C x 16 MM2 | Mtr. | 0.00 | 50.00 |  | 0
104184 | C | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
104185 | C.1 | Supply, Installation, Testing Commissioning of Surface Flush mounting 10kA 25kA (As per Panel requirement) Phase segregated Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on fork type Insulator, Independent neutral busbar for each phase including inter connecting wiring earth bus on insulation mount. Make Brand selection as per Airport TDM listed. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per requirement). |  | 0.00 | 0.00 |  | 0
104186 | C.1.2 | 12 Way TPN Panel Board with 125A 4P RCBO incomer,and outgoings as per SLD Load Calculation Sheet. Make Brand selection as per Airport TDM listed. | Nos. | 0.00 | 1.00 |  | 0
104187 | C.1.3 | 6 Way SPN Panel Board with 20A 2P RCBO incomer and outgoings as per SLD Load Calculation Sheet. Make Brand selection as per Airport TDM listed. | Nos. | 0.00 | 1.00 |  | 0
104188 | D | CIRCUIT MAINS EARTH |  | 0.00 | 0.00 |  | 0
104189 | D.1 | Supply, Installation, Testing Commissioning of Sub Circuit Mains Earth wires with Fire Rated LSH LSZH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back Boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires, etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. Circuit mains shall be measured from DB to switch board, looping between switch board to outlets lights, and looping from switch board to switch board. |  | 0.00 | 0.00 |  | 0
104190 | D.1.2 | 1C x 6 MM2 | Mtr. | 0.00 | 300.00 |  | 0
104191 | E | LIGHT FIXTURES POINT WIRING |  | 0.00 | 0.00 |  | 0
104192 | E.1 | Supply, Installation, Testing Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with Lamps, Ballasts Drivers Starters, Switches Lighting Control Switch Board with Fire Rated LSH LSZH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Wiring shall be as per IS 732. Make Brand selection by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
104193 | E.1.2 | BLACK COLOUR TRACK LIGHT (Point Wiring only) | Nos. | 0.00 | 7.00 |  | 0
104194 | E.1.4 | Ceiling mounted down lights finished in Black 150mm dia LED LIGHT (Point Wiring only) | Nos. | 0.00 | 12.00 |  | 0
104195 | E.1.5 | SIGNAGE LIGHTS (Point Wiring only) | Nos. | 0.00 | 3.00 |  | 0
104196 | E.1.6 | Lighting Control Switch board with switches as required (Point Wiring only) | Nos. | 0.00 | 1.00 |  | 0
104197 | E.1.7 | EXIT LIGHT (Wall Ceiling Mounted) | Nos. | 0.00 | 1.00 |  | 0
104198 | F | WIRING DEVICES (SWITCHES SOCKETS) |  | 0.00 | 0.00 |  | 0
104199 | F.1 | Supply, Installation, Testing Commissioning of Wiring Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture Finishes) with Fire Rated LSH LSZH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Wiring shall be as per IS 732. Make Brand selection as per Airport TDM listed by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
104200 | F.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 0.00 | 16.00 |  | 0
104201 | F.1.3 | 20A SINGLE SWITCHED SOCKET OUTLET industrial socket | Nos. | 0.00 | 18.00 |  | 0
104202 | F.1.8 | BLANK PLATE | Nos. | 0.00 | 3.00 |  | 0
104203 | G | CONTAINMENT (CABLE TRAY, TRUNKING, CONDUITS) |  | 0.00 | 0.00 |  | 0
104204 | G.1 | Supply Installation of GI Cable Tray, GI Cable Trunking, GI Heavy Duty PVC conduits through wall ceiling floor as per drawings, complete with standard accessories factory made fittings, earthing throughout the run with copper braids, wall ceiling suspended supports, etc. Make Brand selection as per Airport TDM listed by Client. |  | 0.00 | 0.00 |  | 0
104205 | G.1.1 | 150 x 50 MM CABLE TRUNKING | Mtr. | 0.00 | 32.00 |  | 0
104206 | G.1.2 | 25 MM GI CONDUIT | Mtr. | 0.00 | 250.00 |  | 0
104207 | H | UPS SYSTEM |  | 0.00 | 0.00 |  | 0
104208 | H.1 | Supply, Installation, Testing Commisioning of 2KVA Single phase UPS with 30 Minute Back-up with SMF Battery Bank + Battery Stand. | Nos. | 0.00 | 1.00 |  | 0
104209 | J | DATA NETWORK SYSTEM |  | 0.00 | 0.00 |  | 0
104210 | J.1 | Supply, Installation, Testing Commissioning of Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. Make Brand selection as per Airport TDM listed by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
104211 | J.1.1 | Dual Data outlet (RJ45) Jack | Nos. | 0.00 | 1.00 |  | 0
104212 | J.1.3 | Patch Cords (1.5 meters length) | Nos. | 0.00 | 9.00 |  | 0
104213 | J.1.4 | CAT 6 Cable | Mtr. | 0.00 | 75.00 |  | 0