## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
167444 | C | AC PIPING AND ACCESSORIES |  | 0.00 | 0.00 |  | 0
167445 |  | AC CONDENSATE DRAIN PIPE |  | 0.00 | 0.00 |  | 0
167446 | C.1 | Supply, installation and testing of Rigid uPVC condensate drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. |  | 0.00 | 0.00 |  | 0
167447 | C.1.1 | 25 mm Ø | Mtr | 0.00 | 4.00 |  | 0
167448 |  | AC CHILLED WATER PIPING |  | 0.00 | 0.00 |  | 0
167449 | C.2 | Supply, installation and testing of MS class (C) Chilled water pipes with insulation of approved make with vapor barrier and finished with protective coating (Pidilite Equivalent) over a layer of 7 Mil glass cloth for mechanical protection complete with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports etc. Piping insulation shall be expanded polyurethane foam with 36 kg m3 minimum density, thickness as specified below, 85% minimum closed cell content and thermal conductivity of 0.019 W m.k at 10°C. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works. |  | 0.00 | 0.00 |  | 0
167450 | C.2.1 | 32 mm Ø - (Insulation - 30 mm thick) | Nos | 0.00 | 6.00 |  | 0
167451 | D | AC PIPING VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
167452 | D.1 | Supply, installation, testing Commissioning of FCU Valve Kit of approved make for HVAC fan coil units in heating cooling systems for FCUs. Complete with pressure independent control valve with proportional linear actuator (Modulating type), three-way shut-off valves, integrated by-pass, Venturi device with pressure test ports , Shut Off valve with Strainer and pre-formed shell insulation made of PPE. Flexible connector with threaded nuts clamps to be provided between the unit and kit of suitable length. |  | 0.00 | 0.00 |  | 0
167453 | D.1.1 | 32 mm Ø | Nos | 0.00 | 1.00 |  | 0
167454 | D.2 | Supply, Installation, Testing, and Commissioning Forged Brass Ball Valve of approved make with full bore lever operated with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled hot water pipe insulation with threaded connection ends with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
167455 | D.2.1 | 32 mm Ø | Nos | 0.00 | 2.00 |  | 0
167456 | D.3 | Supply, Installation, Testing, and Commissioning BTU Meter of approved make with direct pipe connection type or operated via sensor module connected supply and return pipe with all necessary fixing and valve arrangements. LCD display (shows all water parameters), with flow rate, temperature inputs, data storage up to 365 days. The display panel shall be mounted at readable height and it shall include interconnecting wiring between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box with all necessary fixing arrangements. Unit shall be compatible with facility Building Management System. (Make and model shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
167457 | D.3.1 | 32 mm Ø | Nos | 0.00 | 1.00 |  | 0
167458 | D.4 | Supply, Installation, Testing, and Commissioning of Forged Brass Drain Valve Drain Cock, of approved make rubber seal, O rings e with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
167459 | D.4.1 | Drain Valve connected in chilled water supply return line | Nos | 0.00 | 2.00 |  | 0
167460 | D.5 | Supply, Installation, Testing, and Commissioning of Forged Brass Automatic Air Vent of approved make with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
167461 | D.5.1 | Automatic Air Vent connected in chilled water supply return line | Nos | 0.00 | 2.00 |  | 0
167462 | D.6 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
167463 | D.6.1 | Dial Size - 63 mm Ø | Nos | 0.00 | 2.00 |  | 0
167464 | D.7 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
167465 | D.7.1 | Dial Size - 63 mm Ø | Nos | 0.00 | 2.00 |  | 0
167466 | D.8 | Supply, installation, testing commissioning of Test point of approved make with all necessary fixing arrangements.. |  | 0.00 | 0.00 |  | 0
167467 | D.8.1 | Test point for supply and return lines | Nos | 0.00 | 2.00 |  | 0
167468 | E | AIR DISTRIBUTION DUCTS RECTANGULAR DUCTS |  | 0.00 | 0.00 |  | 0
167469 | E.1 | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  | 0.00 | 0.00 |  | 0
167470 | E.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 0.00 | 14.00 |  | 0
167471 | E.1.2 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.mtr | 0.00 | 29.00 |  | 0
167472 | E.2 | Supply, installation, and testing of Black Steel (BS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  | 0.00 | 0.00 |  | 0
167473 | E.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 0.00 | 26.00 |  | 0
167474 |  | FLEXIBLE DUCTS |  | 0.00 | 0.00 |  | 0
167475 | E.3 | Supply, installation, and testing of Insulated Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by air handling units or any other equipment s connected to the duct with air tight fittings with all necessary accessories. |  | 0.00 | 0.00 |  | 0
167476 | E.3.1 | For FCU | Nos | 0.00 | 1.00 |  | 0
167477 | F | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS |  | 0.00 | 0.00 |  | 0
167478 | F.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg m.s.Pa i.e. µ>7000 Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 EN 12086 EN13469. Black Colour with having a density of 50 ± 10 Kg M3. Quote shall be inclusive of necessary Adhesive. |  | 0.00 | 0.00 |  | 0
167479 | F.1.2 | 13 mm thicknesses - (SAD) | Sq.mtr | 0.00 | 14.00 |  | 0
167480 | F.1.2 | 25 mm thicknesses - (FAD) | Sq.mtr | 0.00 | 29.00 |  | 0
167481 | F.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using rockwool with silver foil covering, density of 50 Kg m3.Quoute shall be inclusive of necessary Adhesive. |  | 0.00 | 0.00 |  | 0
167482 | F.2.1 | 25 mm thicknesses - (KEAD) - For Kitchen Exhaust | Sq.mtr | 0.00 | 26.00 |  | 0
167483 |  | AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS |  | 0.00 | 0.00 |  | 0
167484 | F.3 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg m3 Quote shall be inclusive of necessary Adhesive. Thermal conductivity of the insulation material shall not exceed 0.047 W m K at an average temperature of 20°C. |  | 0.00 | 0.00 |  | 0
167485 | F.3.1 | 15 mm thicknesses - (SAD) | Sq.mtr | 0.00 | 4.00 |  | 0
167486 | G | AIR DISTRIBUTION DUCT - DAMPERS DUCT AIR CONTROL DAMPERS |  | 0.00 | 0.00 |  | 0
167487 | G.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper Collar Damper of approved make. |  | 0.00 | 0.00 |  | 0
167488 | G.1.1 | Size - 300 x 300 mm | Nos | 0.00 | 4.00 |  | 0
167489 | G.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. |  | 0.00 | 0.00 |  | 0
167490 | G.2.1 | Size - 250 x 150 mm | Nos | 0.00 | 7.00 |  | 0
167491 | G.2.2 | Size - 300 x 150 mm | Nos | 0.00 | 1.00 |  | 0
167492 | G.2.3 | Size - 350 x 300 mm | Nos | 0.00 | 1.00 |  | 0
167493 | G.2.4 | Size - 400 x 200 mm | Nos | 0.00 | 1.00 |  | 0
167494 | G.2.5 | Size - 400 x 350 mm | Nos | 0.00 | 1.00 |  | 0
167495 | G.2.6 | Size - 500 x 450 mm | Nos | 0.00 | 1.00 |  | 0
167496 | G.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.(For Kitchen Exhaust MS duct) |  | 0.00 | 0.00 |  | 0
167497 | G.3.1 | Size - 250 x 250 mm | Nos | 0.00 | 7.00 |  | 0
167498 | G.3.2 | Size - 300 x 250 mm | Nos | 0.00 | 1.00 |  | 0
167499 | G.3.3 | Size - 350 x 300 mm | Nos | 0.00 | 1.00 |  | 0
167500 | G.3.4 | Size - 600 x 300 mm | Nos | 0.00 | 1.00 |  | 0
167501 | H | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS) |  | 0.00 | 0.00 |  | 0
167502 |  | GRILLES |  | 0.00 | 0.00 |  | 0
167503 | H.1 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar Square Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange frame with 8 mm step suitable to tegular grid type false ceiling with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. |  | 0.00 | 0.00 |  | 0
167504 | H.1.1 | Neck Size - 300 mm X 300 mm - (2 - Way) | Nos | 0.00 | 6.00 |  | 0
167505 |  | LOUVERS |  | 0.00 | 0.00 |  | 0
167506 | H.2 | Supply, installation, and testing of Extruded Aluminium Fresh Air Sand Trap Louver of approved make with Bird screen and Wire mesh with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. |  | 0.00 | 0.00 |  | 0
167507 | H.2.1 | Size - 750 mm X 600 mm | Nos | 0.00 | 1.00 |  | 0
167508 | H.3 | Supply, installation, testing and commissioning of Extruded Aluminium Exhaust Air Louver of approved make with 45 degree blades to avoid rain water penetrations continued with wire mesh and bird screen, 30 mm flange with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer Architect. |  | 0.00 | 0.00 |  | 0
167509 | H.3.1 | Size - 950 mm X 600 mm | Nos | 0.00 | 1.00 |  | 0
167510 | J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
167511 | J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
167512 | J.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 0