## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
167871 | A | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING |  | 0.00 | 0.00 |  | 0
167872 | A.1 | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. |  | 0.00 | 0.00 |  | 0
167873 | B | METER METER PANEL |  | 0.00 | 0.00 |  | 0
167874 | B.1 | Supply, Installation, Testing Commissioning of kWH MFM Energy Meter Panel complete with Enclosure (If required as per site condition Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type and compatible with Airport BMS for realtime monitoring, of approved make or any other make with kVAH option with Approval from TS Department. |  | 0.00 | 0.00 |  | 0
167875 | B.1.1 | 63 5A Energy Meter(Direct)-3 Phase | Nos | 0.00 | 1.00 |  | 0
167876 | C | LV CABLING |  | 0.00 | 0.00 |  | 0
167877 | C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed,AL Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) earthing). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. |  | 0.00 | 0.00 |  | 0
167878 | C.1.1 | 3.5C x 50 Sq. mm XLPE AL Armoured Cable + 2 x 8 SWG CU. | Mtr | 0.00 | 10.00 |  | 0
167879 | C.1.2 | 4C x 4 Sq. mm XLPE CU. Armoured Cable + 2x10 SWG CU. | Mtr | 0.00 | 160.00 |  | 0
167880 | D | CABLE END TERMINATIONS |  | 0.00 | 0.00 |  | 0
167881 | D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete. |  | 0.00 | 0.00 |  | 0
167882 | D.1.1 | 3.5C x 50 Sq. mm XLP Al. Armoured Cable | Nos | 0.00 | 4.00 |  | 0
167883 | D.1.2 | 4C x 4 Sq. mm XLPE CU Armoured Cable | Mtr | 0.00 | 14.00 |  | 0
167884 | E | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
167885 | E.1 | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.), Indicative Devices (Phase Indicative Lamps, kWH Meter, MFM, Voltmeter, Ammeter, Switches, etc.), Control Devices (Bus Coupling Contactors, Earth Leakage, Control, Over Load Relays, Shunt trip coil for BMS, CT, PT, Low Voltage Power Supply Transformers Protective relays, etc.), Starter Panels (DOL Starters, Star Delta Starters, Soft Starters, VFD s, etc), Fire Alarm Interfacing circuit devices relays as per Electrical SLD Load Calculation Sheet. The DBs shall also be fully compatible with the Building Management System (BMS) for integration into the centralized control system, enabling remote monitoring, status indication, fault detections through communication protocols such as Modbus, BACnet, or other airport-specified protocols. This includes provisions for BMS-compatible meters, relays, and communication interfaces as per BMS design.The DB shall include provisions for future BMS upgrades or modifications as per airport operational changes All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). |  | 0.00 | 0.00 |  | 0
167886 | E.1.1 | SMDB-COM16 Way Three phase Panel boardIncomer 100A FP MCCB - 1 No.32A 30 mA FP RCBO - 1 No.(Sub Incomer)Outgoings10 16 20 25A SP MCB- 18 Nos16A 30mA 2P RCBO - 6 Nos.25A 30mA 4P RCBO - 8 Nos. | Each | 0.00 | 1.00 |  | 0
167887 | E.1.2 | UPS DB-0116 Way SPN DBIncomer 25A 30mA 2P RCBO - 1 No.Outgoings10 16 20 25A SP MCB- 12 Nos | Each | 0.00 | 1.00 |  | 0
167888 | F | LIGHT POINT WIRING |  | 0.00 | 0.00 |  | 0
167889 | F.1 | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade using 2 X 1.5 Sq mm PVC insulated fine stranded single core FRLSH copper conductor wires phase and neutral and with 1.5 Sq mm PVC insulated, green coloured, fine stranded single core copper cable as earth continuity, earth wire crimped to copper socket, fastened using brass bolt and nut etc through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
167890 | F.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. | Nos | 0.00 | 8.00 |  | 0
167891 | F.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) | Nos | 0.00 | 135.00 |  | 0
167892 | G | CIRCUIT WIRING |  | 0.00 | 0.00 |  | 0
167893 | G.1 | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. |  | 0.00 | 0.00 |  | 0
167894 | G.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit GI Trunking from DB to Light control switch box Normal Sockets. | Mtr | 0.00 | 390.00 |  | 0
167895 | G.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit GI Trunking from DB to Power points. | Mtr | 0.00 | 100.00 |  | 0
167896 | H | POWER POINTS (SWITCHES SOCKETS) |  | 0.00 | 0.00 |  | 0
167897 | H.1 | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. |  | 0.00 | 0.00 |  | 0
167898 | H.1.1 | 13A Single Switched Socket Outlet | Nos | 0.00 | 0.00 |  | 0
167899 | H.1.2 | 13A Dual Switched Socket Outlet | Nos | 0.00 | 3.00 |  | 0
167900 | H.1.3 | 16A Single Switched Socket Outlet | Nos | 0.00 | 2.00 |  | 0
167901 | H.1.4 | 20A Isolator with suitable metal enclosure | Nos. | 0.00 | 1.00 |  | 0
167902 | H.1.5 | One Gang Blank Plate | Nos | 0.00 | 1.00 |  | 0
167903 | J | LIGHTING FIXTURES |  | 0.00 | 0.00 |  | 0
167904 | J.1 | Installation, testing and commissioning of approved makes Light fixtures complete with accessories. Rate shall include necessary mounting bracket, suspension chains etc. |  | 0.00 | 0.00 |  | 0
167905 | J.1.1 | Exit Light (Wall Ceiling Mounted) | Nos | 0.00 | 3.00 |  | 0
167906 | K | CONTAINMENT |  | 0.00 | 0.00 |  | 0
167907 | K.1 | Supply Installation of approved makes medium duty Hot dip perforated GI Cable Tray, through Wall Ceiling as per drawings, complete with standard accessories factory made fittings, earthing throughout the run with copper braids, wall ceiling suspended supports, etc. |  | 0.00 | 0.00 |  | 0
167908 | K.1.1 | 300 x 50 mm Cable Tray | Mtr. | 0.00 | 8.00 |  | 0
167909 | K.1.2 | 150 x 50 mm Cable Tray | Mtr. | 0.00 | 6.00 |  | 0
167910 | K.1.3 | 100 x 50 mm Cable Tray | Mtr. | 0.00 | 45.00 |  | 0
167911 | L | UPS SYSTEM |  | 0.00 | 0.00 |  | 0
167912 | L.1 | Supply, Installation, Testing Commissioning of approved makes UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) standard accessories equipments required for complete functioning of the system, earthing, support system (if required), etc. The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. |  | 0.00 | 0.00 |  | 0
167913 | L.1.1 | 5 KVA Single phase UPS with 30 Minute Back-up | Nos. | 0.00 | 1.00 |  | 0
167914 | N | DATA NETWORK SYSTEM |  | 0.00 | 0.00 |  | 0
167915 | N.1 | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
167916 | N.1.1 | Single Data outlet (RJ45) Jack | Nos | 0.00 | 0.00 |  | 0
167917 | N.1.2 | Dual Data outlet (RJ45) Jack | Nos | 0.00 | 3.00 |  | 0
167918 | N.1.3 | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | Mtr. | 0.00 | 190.00 |  | 0
167919 | O | PA SYSTEM |  | 0.00 | 0.00 |  | 0
167920 | O.1 | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  | 0.00 | 0.00 |  | 0
167921 | O.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories | Nos | 0.00 | 4.00 |  | 0
167922 | O.1.2 | Volume Controller | Nos | 0.00 | 1.00 |  | 0
167923 | O.1.3 | PA Controller with Amplifier | Nos | 0.00 | 1.00 |  | 0
167924 | O.1.4 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | Mtr. | 0.00 | 40.00 |  | 0
167925 | P | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
167926 | P.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
167927 | P.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 0
167928 | Q | MISCELLANEOUS |  | 0.00 | 0.00 |  | 0
167929 | Q.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. |  | 0.00 | 0.00 |  | 0
167930 | Q.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Unit | 0.00 | 1.00 |  | 0
167931 | Q.1.2 | Provide and Fixing Shock Treatment Chart | Unit | 0.00 | 1.00 |  | 0
167932 | Q.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side | Unit | 0.00 | 1.00 |  | 0