## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
41299 |  | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS SPECIFICTIONS) |  | 0.00 | 0.00 |  | 0
41300 | 1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support. |  | 0.00 | 0.00 |  | 0
41301 |  | 24G sheet | sq.m | 0.00 | 40.00 |  | 1450
41302 |  | 26G sheet | sq.m | 0.00 | 5.00 |  | 1350
41303 | 2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required 24G sheet | sq.m | 0.00 | 5.00 |  | 1450
41304 | 3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.00 | 1.00 |  | 2500
41305 | 4 | Supplying fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 0.00 | 1.00 |  | 2500
41306 | 5 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 0.00 | 1.00 |  | 2250
41307 | 6 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Return air Grilles without volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 0.00 | 2.00 |  | 2500
41308 | 7 | Supply, installation and testing of Acoustic lining with Open cell nitrile rubber with in supply and return air ducts of specified thickness as per the specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as perthe specifications 15 mm thick | sq.m | 0.00 | 10.00 |  | 760
41309 | 8 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber(Class“O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. 19mm thick | sq.m | 0.00 | 40.00 |  | 1050
41310 | 9 | Supplying, installing and testing of UPVC pipe ( heavy duty) with 6 mm thick nitrile rubber insulation with protective coating on condensing water piping and fitting like bends, elbow, tee and union, etc. as per the approved shop drawings and specifications. 25mm Dia | Rmt | 0.00 | 5.00 |  | 450
41311 | 10 | Supply ,Installation ,Testing and commissioning of ERW heavy duty C Class MS pipes as per IS-1239 upto 6 dia. and as per IS-3589 above 6 dia. cut to required lengths and installed with all welded joints, complete with necessary pipe hot dip galvanized MS supports, GI hangers with rubber lined universal clamps and hangers , fittings like bends, elbows, tees, reducers, matching flanges, neoprene 6 mm thick gaskets, hot dipped galvanized nut blots washers ,PUF gutti with U clamp, socket and fittings for instruments and sensors connections etc. ERW pipes shall be with two coats of Zinc Chromate paint for anti-rust including all fittings like valves, flanges and unions, etc. Note Pipe Measurement are in Pair (Supply + Return) . Quoted rates shall be inclusive of the cost of piping Insulation of Class O rated thermal insulations with one sided factory laminated glass clothed Nitrile Rubber insulation with density 45-60 kg m3 with covered with two coats of UL Listed lag coating (Low VOC) Anti-fungal, Anti-microbial vapour barrier for line item sealed with acrylic based food grade sealant. 32 mm dia MS Pipe with 25 mm thick Insulation | Rmt | 0.00 | 10.00 |  | 1650
41312 | 11 | Providing and fixing in position following ball valves 32 mm dia valves | Nos. | 0.00 | 2.00 |  | 1500
41313 | 12 | Providing and fixing in position the following ‘Y’ Strainers 32 mm dia strainers | Nos. | 0.00 | 1.00 |  | 8000
41314 | 13 | Supplying, installation, testing and commissioning of Auto air vents. 25 mm dia pipes | Nos. | 0.00 | 1.00 |  | 1250
41315 | 14 | Providing and fixing in position SS 304 the industrial dial type pressure gauges with gun metal valves. | Nos. | 0.00 | 2.00 |  | 3000
41316 | 15 | Providing and fixing in position SS 304 the mercury-in- glass industrial dial type thermometers. | Nos. | 0.00 | 2.00 |  | 3000
41317 | 16 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display fan speed control, capable of providing individual space temperature control for cooling application. The controller shall produce a dual output to cooling coils in response to load change in rooms. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water duty . (minimum of 5 Deg F dead band ) | No. | 0.00 | 1.00 |  | 13500
41318 | 17 | Supply, installation, testing and commissioning of Electronic Self Balancing Valve pressure independent with independent type dynamic balancing valve for AHUs with integrated 2 way modulating control valves in a single body. The actuator shall be capable of accepting 2-10 VDC 4-20 mA electric signal and shall provide similar transduced feedback output signal to control system for flow measurement. The minimum close off pressure actuator must be 1.5 times shut off head of pump 5 bars whichever is maximum. The valves shall be suitable for following pipe sizes 32 mm dia | No. | 0.00 | 1.00 |  | 9050
41319 | 18 | Supply, Installation, Testing and Commissioning of BMS compatible ultrasonic BTU Meter complete with flanged type water flow meter (pressure drop across water meter not exceeding 0.1 bar at the specified nominal flow rate), temperature sensors, LCD display panel, inbuilt Lithium battery backup with minimum six years life. The units shall be capable to calculate and store maximum values, display flow rates and temperature difference across supply and return. The quoted price shall be inclusive of necessary wiring, conduiting between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box. The size of the BTU meter is as under 32 mm dia BTU Meter | No. | 0.00 | 1.00 |  | 45000
41320 | 19 | CONTROL PANEL FOR AHU (WITH DOL SD STARTER) Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing terminating into MCCB in each panel shall be provided by the electrical contractor. All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included. All outgoing shall be provided with Stop Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. The panel shall include the following components and accessories. a)MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA. b)DOL SD starter as per HP ratings c) Terminal block for power distribution. d) Contactor, over load relay with built in single phasing protection. e) Phase indicating lights and indicating light for ON status. f) Digital voltmeter and digital ammeter with selector switches. g) Time delay relay for delayed automatic restart of air handling unit motor. h) For on off remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. i) All starters shall be provided with suitable potential free contract for connections to the Building Automation System. The number of AHU FAN control panels shall be as follows. 2 HP DOL Starter | No. | 0.00 | 1.00 |  | 34000