## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
161395 | 1.1 | Providing fixing glazed vitreous china single trap syphonic pattern having back inlet ,supporting chair ,wall hung water closet with cistern complete with all internal fittings accessories and CP brass flush bend (European type) water closet with seat and lid, with C.P. brass hinges and rubber buffers, adapter, rubber joints fixed to W.C., C.P. brass screwed washers including cutting and making good the walls and floors wherever required and HDPE wc pan connector including jointing with white cement coomplete in all respects. Wall hung W.C. pan (White colour)with white plastic seat lid Thermoset moulded ( bakelite ) IS 2548 Part I For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 3.00 |  | 28500
161396 | 1.2 | Providing fixing glazed vitreous china wash basin with R.S. or C.I. brackets painted white, 32mm C.P. brass waste of standard pattern, 32 mm dia. C.P. brass bottle trap(Jaquar model no ALD 769L) and union 32 mm dia C.P. pipes to wall flange. complete including cutting and making good the walls wherever required.Undercounter wash basin (White colour)of size 585x430 mm. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 3.00 |  | 22500
161397 | 1.5 | Providing fixing Sink Mixer with Swinging Casted Spout (Table Wall Mounted) with 450mm long Copper Pipes Brass Nuts. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 16.00 |  | 6780
161398 | 1.6 | Providing fixing 15 mm dia C.P. brass angle valves with 450mm long C.P. Copper connecting pipe union nut C.P. cast brass wall flange. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 40.00 |  | 4250
161399 | 1.7 | Providing fixing toilet paper holder including cutting and making good the walls. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 3.00 |  | 3250
161400 | 1.8 | Providing fixing C.P. brass twin coat hooks fixed on toilet door with C.P. brass screws. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 3.00 |  | 1450
161401 | 1.1 | Providing fixing beveled edge mirror 5.5mm thick of superior quality plate glass complete with 6mm thick marine ply sheet ground fixed to wooden cleats with CP brass screws and washerswith 40 mm wide teak wood frame as per design including polishing. For supply, installation, testing commissioning of sanitary fixtures as per above details | Sqm | 0.00 | 3.00 |  | 10222
161402 | 1.11 | Providing fixing Health Faucet with 8mm dia, 1M long PVC tube and wall hook. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 3.00 |  | 4500
161403 | 1.12 | Providing fixing, testing and commissioning of storage type electric water heater with automatic thermostatic control electric element, pressure release valve, brackets fixed to expansion fasteners with M.S. nuts and bolts all complete including cutting and making good the walls wherever required. |  | 0.00 | 0.00 |  | 0
161404 |  | 50 litres capacity For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 6.00 |  | 27500
161405 |  | 100 litres capacity For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 1.00 |  | 48000
161406 | 1.13 | Providing fixing 15 mm dia C.P. brass bib cock with Hose union of approved quality. For installation, testing commissioning of sanitary fixtures as per above details. | Each | 0.00 | 5.00 |  | 3650
161407 | 1.14 | Providing fixing 15 mm dia C.P. brass bib cock with C.P. wall flange of approved quality. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 5.00 |  | 3450
161408 | 1.15 | Providing fixing 15mm C.P. brass push tap for basin with 450mm long copper pipes and brass nuts. For supply, installation, testing commissioning of sanitary fixtures as per above details | Each | 0.00 | 3.00 |  | 3500
161409 |  | NOTE - Detail of Sanitary fixture are for the information of the Contractor,however model makes of all sanitary fixtures shall be selected by Architect Interior designer Project manager and the same shall be binding for execution. No additional fixing cost shall be paid for change in type of sanitary fixtures. Contractor to receive all the above mentioned items store at place as directed at site in case supply is by Client . |  | 0.00 | 0.00 |  | 0
161410 |  | SUB HEAD B WATER SUPPLY |  | 0.00 | 0.00 |  | 0
161411 | 1 | Providing and fixing Chlorinated polyvinyl Chloride (CPVC) pipes-SDR-11,havings thermal stability for hot cold water supply including all CPVC plain brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing.This includes jointing of pipes fittings with CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in charge,fixing at wall ceiling level supported by clamps, hangers, structural steel supports, etc.Cost shall include making connections with Sanitary fixtures CP fittings. |  | 0.00 | 0.00 |  | 0
161412 |  | b) 20 mm outer dia | RM | 0.00 | 450.00 |  | 950
161413 |  | c) 25 mm outer dia | RM | 0.00 | 100.00 |  | 1050
161414 |  | d) 32 mm outer dia | RM | 0.00 | 80.00 |  | 1175
161415 |  | e) 40 mm outer dia | RM | 0.00 | 180.00 |  | 1250
161416 |  | f) 50 mm outer dia | RM | 0.00 | 25.00 |  | 1658
161417 |  | g) 65mm inner dia-sch 40 with sch 80 fittings | RM | 0.00 | 20.00 |  | 1765
161418 | 2 | Providing fixing gun metal lever operated ball valve. Tested to a pressure of 15 Kg Sqcm. Including flanges union, nuts, bolts, washer etc. Complete as required. |  | 0.00 | 0.00 |  | 0
161419 |  | a) 15 mm dia | NOS | 0.00 | 4.00 |  | 3250
161420 |  | b) 20 mm dia | NOS | 0.00 | 8.00 |  | 3485
161421 |  | c) 25 mm dia | NOS | 0.00 | 4.00 |  | 3565
161422 |  | d) 32 mm dia | NOS | 0.00 | 4.00 |  | 3625
161423 |  | e) 40 mm dia | NOS | 0.00 | 8.00 |  | 3758
161424 |  | f) 50 mm dia | NOS | 0.00 | 8.00 |  | 4125
161425 | 3 | Providing fixing gunmetal non return valve including all accessories suitable for working pressure of 15 Kg sqcm of the following sizes |  | 0.00 | 0.00 |  | 0
161426 |  | c) 40mm dia | NOS | 0.00 | 2.00 |  | 4250
161427 | 4 | Supplying, installing, testing and commissioning of triple layer HDPE water storage tank including holes for inlet, outlet, overflow level indicator drain and vent points, manhole cover suitable supporting structure complete.Bottom of tank shall be atleast 450mm above finish floor level of terrace. |  | 0.00 | 0.00 |  | 0
161428 |  | a) Capacity 5000 Lts. | SET | 0.00 | 6.00 |  | 62500
161429 | 5 | Providing and fixing electronic type level indicator for water tank mounted in panel with level display, alarm when water level is low or high, full range from one level to four level display and manual reset for alarm etc. with electrical wiring conduit supports from wall ceiling probs and all other accessories complete as required. | NOS. | 0.00 | 3.00 |  | 12500
161430 | 6 | Providing fixing 6mm thick nitryl rubber insulation on hot water pipes-15 to 25 mm dia pipes burried inside walls. | RM | 0.00 | 200.00 |  | 125
161431 | 7 | Providing and fixing 24 SWG Al. sheet metal cladding over pipe insulation, 50mm overlapped and hold the same with self-tapping screws and all joints to be sealed with sealent (tarfelt strip) complete as required. |  | 0.00 | 0.00 |  | 0
161432 |  | a) 15 mm dia pipe --- SP insulation 25 mm thick | RM | 0.00 | 20.00 |  | 1350
161433 |  | b) 20 mm dia pipe --- SP insulation 25 mm thick | RM | 0.00 | 100.00 |  | 1450
161434 |  | c) 25 mm dia pipe --- SP insulation 25 mm thick | RM | 0.00 | 10.00 |  | 1625
161435 |  | d) 32 mm dia pipe --- SP insulation 25 mm thick | RM | 0.00 | 10.00 |  | 1850
161436 |  | e) 40 mm dia pipe --- SP insulation 25 mm thick | RM | 0.00 | 40.00 |  | 2075
161437 |  | f) 50 mm dia pipe --- SP insulation 25 mm thick | RM | 0.00 | 10.00 |  | 2280
161438 | 8 | Providing fixing of CI butterfly valve suitable for pressure 15 Kg Sqcm. with flanges, nut bolts gaskets complete required. |  | 0.00 | 0.00 |  | 0
161439 |  | a) 65 mm dia | NOS | 0.00 | 2.00 |  | 6500
161440 | 9 | Providing fixing electricaly operated Motorized Butterfly Valves with by pass piping all fittings , by pass valves (3nos) for filling of overhead tanks complete with High Low level control switches to control the valves. The level controllers shall be installed in overhead tanks.The system should be complete in all respect with accessories ,220 volt V AC 24 volt DC , IP67 electrical water level control unit , copper control wiring in wheather proof casing etc. from butterfly valves to control unit . |  | 0.00 | 0.00 |  | 0
161441 |  | a) 32 mm dia | NO | 0.00 | 1.00 |  | 14500
161442 |  | b) 40 mm dia | NO | 0.00 | 1.00 |  | 18500
161443 | 10 | Providing fixing digital water flow meter on pipes of following diameter. |  | 0.00 | 0.00 |  | 0
161444 |  | a) 25 mm dia | NO | 0.00 | 1.00 |  | 9500
161445 |  | b) 32 mm dia | NO | 0.00 | 1.00 |  | 11500
161446 |  | c) 40 mm dia | NO | 0.00 | 1.00 |  | 14000
161447 | 11 | Providing and fixing in position G.I. vent with brass mosquito proof coupling and air filter including return bend, complete as required. The entire fitting shall be hot dipped galvanised. |  | 0.00 | 0.00 |  | 0
161448 |  | a) 50 mm dia | NOS | 0.00 | 6.00 |  | 12500
161449 |  | SUB HEAD C INTERNAL DRAINAGE (SOIL, WASTE VENT PIPES) |  | 0.00 | 0.00 |  | 0
161450 | 1 | Providing, fixing, jointing and testing in position of ISI marked UV stabilized UPVC pipes for soil, waste and vent, Type-B as per IS 13592 suitable for rubber ring joints, including all neccessary specials and fittings (confirming to IS 14735) i.e. bends, tees, junctions (with or without doors), reducers, WC connectors, couplers, cowls, clamps, rubber rings, clean outs ,access pieces at ends of main pipes (for roding) etc. fixing at wall ceiling floor level supported by clamp, hangers structural steel supports etc. in concealed inside duct under floor basement ceiling external work etc. including chase cutting as required, excavation and back filling in all kind of soils, suspended from floor under false ceiling or embedding the pipes laid under floors building in 75 mm. alround 1 2 4 cement concrete (1 cement 2 coarse sand 4 graded stone aggregate 20 mm nominal size) including cost of shuttering for proper completion of the work, breaking and making good the walls and floors etc. after pipes have been duly laid and tested. The rubber ring shall confirm to IS 5382. |  | 0.00 | 0.00 |  | 0
161451 |  | The Pipes will be supported with threaded G I rods clamps on 50x50x5 mm slotted angle. The cost will include all support arrangements. The work includes commissioning of all pipes lines as per drawings and specifications and as directed by engg-in-charge at site. |  | 0.00 | 0.00 |  | 0
161452 |  | a) 75 mm outer dia | RM | 0.00 | 5.00 |  | 2240
161453 |  | b) 110 mm outer dia | RM | 0.00 | 130.00 |  | 1750
161454 |  | c) 160 mm outer dia | RM | 0.00 | 70.00 |  | 3520
161455 | 2 | Providing and laying 1 2 4 cement conc. 100 mm thick all round the pipe including 100mm thick bed concrete for the following M.S. C.I. C.I. class L.A. UPVC pipes and specials below floor including necessary shuttering etc. complete as required. |  | 0.00 | 0.00 |  | 0
161456 |  | a) 75 mm dia pipe | RM | 0.00 | 5.00 |  | 2350
161457 |  | b) 100 mm dia pipe | RM | 0.00 | 100.00 |  | 2450
161458 |  | c) 160 mm outer dia | RM | 0.00 | 70.00 |  | 3250
161459 | 3 | Providing, fixing, jointing and testing in position ISI marked (IS 4985) UPVC pipes of min 6 Kg Sqcm rating with fitting for waste pipe from fixtures to floor trap including reduces, enlarger, socket, couplers, bends, tees etc including fixing at wall ceiling level supported by clamp hangers etc. cutting holes in wall floors slabs and making good the same with cement concrete 1 2 4 complete as required. |  | 0.00 | 0.00 |  | 0
161460 |  | a) 40 mm outer dia | RM | 0.00 | 20.00 |  | 1275
161461 |  | b) 50 mm outer dia | RM | 0.00 | 90.00 |  | 1350
161462 |  | c) 63 mm outer dia | RM | 0.00 | 20.00 |  | 1460
161463 | 4 | Providing fixing UPVC Floor trap of self cleansing design with CP Jali complete in all respects. (Make Supreme Finolex Prince).Multi trap connection to be provided with each floor trap. |  | 0.00 | 0.00 |  | 0
161464 |  | a) 100 mm inlet and 100 mm outlet. | NOS | 0.00 | 36.00 |  | 1850
161465 |  | b) 100 mm inlet and 75 mm outlet. | NO | 0.00 | 2.00 |  | 1650
161466 | 5 | Providing fixing 100m x 50mm PVC waste including cutting chases, the floor slab complete as required. | NOS | 0.00 | 46.00 |  | 1900
161467 | 7 | Providing and fixing PVC clean out plug with suitable inlet key for opening male threaded joint with pipe socket complete as required. |  | 0.00 | 0.00 |  | 0
161468 |  | a) 100 mm dia | NOS | 0.00 | 2.00 |  | 2450
161469 |  | SUBHEAD D EXTERNAL SEWAGE |  | 0.00 | 0.00 |  | 0
161470 | 1 | Providing fixing, jointing and testing in position the following DWC SN8 pipes conforming to IS 16098-Part II for drainage cut to required lengths including all necessary fittings and specials such as bends, junctions, offsets, making proper connections. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil, dewatering, refilling, watering, ramming removing the surplus excavated material and making good the same complete as required. For external sewer. |  | 0.00 | 0.00 |  | 0
161471 |  | b) 160 mm dia pipe | RM | 0.00 | 6.00 |  | 2850
161472 |  | c) 200 mm dia pipe | RM | 0.00 | 30.00 |  | 3350
161473 | 2 | Providing and laying 150 mm thick cement concrete 1 4 8 (1 cement 4 fine sand 8 graded stone aggregate 40mm nominal size) alround pipes including 150 mm thick bed concrete as per standard design.For external sewer. |  | 0.00 | 0.00 |  | 0
161474 |  | b) 150 mm dia pipe | RM | 0.00 | 6.00 |  | 750
161475 |  | c) 200 mm dia pipe | RM | 0.00 | 30.00 |  | 1050
161476 | 3 | Providing and fixing stoneware gully trap grade A of the following sizes with C.I. grating embedded in brick masonary chamber of required size and trap to be set in cement concrete 1 2 4, both side 12mm thick plastering with floating cast of neatcement,rough plaster on outer surface. Making necessary connections providing water tight C.I. cover with frame. Including necessary excavation Including necessary excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. |  | 0.00 | 0.00 |  | 0
161477 |  | a) 180X150 mm outlet -chamber size 450x450mm | NO | 0.00 | 1.00 |  | 5500
161478 | 4 | Constructing brick masonry inspection chamber of the following sizes in brick work of class 75 in cement mortar 1 5 work in cement mortar 1 5 (1 cement 5 fine sand), R.C.C. top slab with 1 2 4 mix (1 cement 2 coarse sand 4 graded stone aggregate 20mm. nominal size) foundation concrete 1 4 8 mix(1 cement 4 coarse sand 8 size).Inside plastering 12 mm thick with cement motor 1 3 ( 1 cement 3 coarse sand) and rough plastering on outside with a floating coat of neat foot rests at 300 mm spacing, banching and making channels with 1 2 4 cement concrete neatly finished, including excavation, in all kind of soil (hard rock), dewatering, refilling, watering, ramming and removing the surplus excavated cement providing MS material making good the same complete as required. |  | 0.00 | 0.00 |  | 0
161479 |  | b) Inside size 90x80 cm ( upto 90 cm maximum depth). | NOS | 0.00 | 3.00 |  | 32500
161480 |  | c) Extra over b above for depth exceeding 60 cm upto 90 cm. | RM | 0.00 | 1.00 |  | 28500
161481 | 5 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS 10910 on 12 mm dia steel bar conforming to IS 1786 having minimum cross section as 23 mm X 25 mm and over all minimum length 263 mm and width as 165 mm with minimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture s permanent identification mark to be visible even after fixing, including fixing in manholes with 30 X 20 X 15 cm cement concrete block 1 3 6 (1 cement 3 coarse sand 6 graded stone aggregate 20 mm nominal size) complete as per design. | NOS | 0.00 | 10.00 |  | 3650
161482 | 6 | Providing fixing in positon precast R.C.C. manhole cover and frame of required shape and approved quality. |  | 0.00 | 0.00 |  | 0
161483 | 7 | Providing fixing cast iron manhole cover with frame. |  | 0.00 | 0.00 |  | 0
161484 |  | a) Medium duty double seal of size 500mm internal diameter.Total weight of cover frame to be not less than 116 Kg. | NOS | 0.00 | 3.00 |  | 16500
161485 | 8 | Constructing Oil Grease Chamber size 2500x 1000mm internal size of 1000mm depth in First class brick work with cement mortar (1 5) Inside 12mm thick with cement mortar 1 3 with floating coat of neat cement and rough plaster on outside, RCC top slab with 500mm dia medium duty manhole cover with frame (weight of cover 58 kg. weight of frame 58 kg.), 150mm thick foundation concrete (1 4 8), necessary excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. | NOS | 0.00 | 2.00 |  | 55000
161486 | 9 | Providing fixing SS 304 chamber with SS 304 manhole cover with frame,inlet outlet connections as per drawing including all associated civil works. | NOS | 0.00 | 13.00 |  | 18500
161487 |  | SUB-HEAD E PUMPS EQUIPMENTS |  | 0.00 | 0.00 |  | 0
161488 | 1 | Supplying, installing, testing commissioning Horizontal centrifugal pump set with C.I. casing, Bronze Impeller, SS shaft suitable for operation on 400 440 volts, 3 phase 2900 RPM electric motor,100 mm dia pressure guage, G.M. isolation cock complete as required. Cyclic operations shall be provided for each set of two pumps.Cost shall included electrical control panel with wiring cabelling control cabelling. |  | 0.00 | 0.00 |  | 0
161489 |  | Raw Water Pumps Location - Plant room at terrace level Number of Pumps = 2 Nos Capacity 2 LPS each Head 25 Mts RPM 2900 | SET | 0.00 | 1.00 |  | 140000
161490 |  | NOTES FOR ALL PUMPS - a) Level Controller with sufficient nos. of low high level alarms, contacts with electrodes and control wiring for the automatic operation of all water supply pumps to achieve the functional requirement shall be provided. Control wiring between these pumps and water tanks shall be provided. Raw water pumps must start at low level of water in domestic water tank stop at high water level in that tank. Dry running protection shall be provided for the pumps. |  | 0.00 | 0.00 |  | 0
161491 | 3 | Providing, fixing, testing commissioning of vertical FRP pressure filter complete with initial charge of filter media frontal piping with valves including testing kit, complete as required.(Location plant room at terrace level). a) Filter for Domestic Water. Tested pressure 6Kg Sq.cm Capacity 2 LPS. | SET | 0.00 | 1.00 |  | 80000
161492 | 4 | Supply, installation, testing commissioning of chlorine dosing system consisting of one FRP HDPE tank of 100 liters capacity with a positive displacement diaphragm Dosing pump with a variable flow rate of 0-12 LPH. The motor shall be suitable for operation at 240 V one phase 50 Hertz supply. The pump shall be supplied complete with necessary poly propylene piping, valves, strainers injection fittings for system to dose solution to the feed line. The pump shall be Asia LMI make. (Location plant room at terrace level). | SET | 0.00 | 1.00 |  | 165000
161493 | 5 | Providing, fixing, testing commissioning of FRP body water softener with frontal piping valves complete with Resin, Hydraulic Brine Injector, HDPE Brine tank of capacity one generation,Remi make mixing motor and all other accessories complete as required. a) Softner for domestic water. Location -Plant Room at terrace level. Input water Hardness(appx) =700 Mg L ( Max )-Exact hardness will be after receiving water analysys report. Output water Hardness 70 ppm Regeneration Period After 1.0 lac lts Operating Pressure 3.5 Kg. per sq.cm Test Pressure 6 Kg. Sq.cm. Capacity 2 LPS | SET | 0.00 | 1.00 |  | 175000
161494 | 6 | Providing fixing packaged Reverse Osmosis System skid mounted complete with pre and post water treatment plant, RO plant feed pumps(2nos.)CIP system, pipes ( SS -High pressure, PVC- low Pressure ) , dosing units,TDS meter, valves, control wiring, electrical panel, instrumentation input output water quality monitoring meters indicators, fully automated. -Location-Plant room at terrace level. TDS of Input(raw) water as per water test report= 600 ppm. Permeate flow rate 1000 LPH (TDS at output after blending will be below 70ppm). Water Test Report-to be obtained from site before finalising technical details of RO plant. RO Plant as mentioned above | NO | 0.00 | 1.00 |  | 215000