## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
56501 |  | The main fire fighting sprinkler riser pipe including floor isolation valve, flow indicating switch, inspectors-test-cum-drain assembly and drain pipe in vertical shafts have already been installed by the main builder. The interior contractor needs to make connections, alteration to existing main network only. All works to be done after seeking permission from building manitenance agency. |  | 0.00 | 0.00 |  | 0
56502 | 4.1 | Providing, fixing, jointing and testing of (Class-C Heavy duty) MS Pipe IS 1239 3589 marked, with accessories like tees, elbows, flanged joints, reducers, compressed asbestos gaskets, nuts and bolts including using modular pipe support. complete as required for delivery suction manifold relating to the pumps including painting of two coats of Red Oxide including all civil breakages and making good the same. The rate includes the cost of installing DI threaded fittings UL listed FM approved for pipe sizes upto 50mm dia and welded joint abov jointing pipe sizes above 50mm dia. All work is to be carried out as per the specifications (Make HSL, Mukut, Lalit steel ) |  | 0.00 | 0.00 |  | 0
56503 |  | The support channel should be made up of cold rolled steel of quality DX51 or greater. The Support channel should be pre-galvanised with minimum GSM of 275 and should have universal mounting slot on the front of the rail for accurate positioning of fasteners and system compatible round and long holes on back of the rail the pipe. |  | 0.00 | 0.00 |  | 0
56504 |  | The pipe clamps should be split type with EPDM inner rubber lining, FM UL approved. |  | 0.00 | 0.00 |  | 0
56505 |  | Threaded rod should be of 4.8 stregth class and necessary accessories should be of 8.8 strength class. |  | 0.00 | 0.00 |  | 0
56506 |  | a. DI Threaded Fittings for pipe size upto 50mm dia |  | 0.00 | 0.00 |  | 0
56507 |  | b. Welded joint above 50mm diameter pipe. |  | 0.00 | 0.00 |  | 0
56508 | 4.1.1 | 25 mm nominal bore | Metre | 0.00 | 55.00 |  | 750
56509 | 4.1.2 | 32 mm nominal bore | Metre | 0.00 | 5.00 |  | 850
56510 | 4.1.3 | 40 mm nominal bore | Metre | 0.00 | 10.00 |  | 1050
56511 | 4.1.4 | 50 mm nominal bore | Metre | 0.00 | 15.00 |  | 1250
56512 | 4.1.5 | 65 mm nominal bore | Metre | 0.00 | 15.00 |  | 1650
56513 | 4.2 | Providing and fixing 15 mm dia gunmetal quick response sprinkler head with quartz bulb and set to operate at specified temperature. Sprinkler head shall carry UL-FM approval (Make Ansul, Buckeye, Smog Hog, Gem-Tyco, ) |  | 0.00 | 0.00 |  | 0
56514 |  | Temperature of operation 68 deg.C. |  | 0.00 | 0.00 |  | 0
56515 | 4.2.1 | Chrome plated pendent type with powder coated twin rosette plate. | Each | 0.00 | 10.00 |  | 250
56516 | 4.2.2 | Upright type sprinkler head | Each | 0.00 | 10.00 |  | 950
56517 | 4.3 | Providing and fixing 25 mm dia, UL-FM approval flexible stainless steel (SS 304) pipe for making final connection of sprinkler head with sprinkler system piping network including 2 nos. 25mm diameter G.I. connector, G.I. Nipple, Reducer, elbow and threaded jointing complete as per detail. (Make Ansul, Buckeye, Smog Hog, Gem-Tyco, ) |  | 0.00 | 0.00 |  | 0
56518 | 4.3.1 | 1000mm long | Each | 0.00 | 5.00 |  | 2050
56519 | 4.3.1 | 1500mm long | Each | 0.00 | 5.00 |  | 2650
56520 | 4.4 | Dismantling and refixing of existing MS pipes including all works like welding, support fixing, painting, testing complete in all respects. |  | 0.00 | 0.00 |  | 0
56521 | 4.4.1 | 25 mm nominal bore | Metre | 0.00 | 5.00 |  | 250
56522 | 4.4.2 | 32 mm nominal bore | Metre | 0.00 | 5.00 |  | 350
56523 | 4.4.3 | 40 mm nominal bore | Metre | 0.00 | 5.00 |  | 450
56524 | 4.4.4 | 50 mm nominal bore | Metre | 0.00 | 5.00 |  | 650
56525 | 4.5 | Making connection with existing main header including butterfly valve, flanges and accessories required.[Make ZOLOTO SANT DRP] |  | 0.00 | 0.00 |  | 0
56526 | 4.5.1 | 65 mm nominal bore | Each | 0.00 | 1.00 |  | 6500
56527 | 4.6 | Providing and fixing brass ball valve with SS 304 Stem and ball, teflon seat complete (PN-16).[Make ZOLOTO SANT DRP] |  | 0.00 | 0.00 |  | 0
56528 | 4.6.1 | 25 mm dia nominal bore | Each | 0.00 | 1.00 |  | 2050
56529 |  | TOTAL FOR S. IV CARRIED OVER TO SUMMARY |  | 0.00 | 0.00 |  | 0