## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
166419 |  | AUTOMATIC FIRE SPRINKLER HEADS ACCESSORIES |  | 0.00 | 0.00 |  | 0
166420 | B.1 | Supply, Installation, Testing Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1 2 NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured Certified to UL 199. Shall also include suspending arrangement with ceiling wall etc. |  | 0.00 | 0.00 |  | 0
166421 | B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 0.00 | 4.00 |  | 0
166422 |  | FIRE SPRINKLER PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
166423 | B.2 | Supply, Installation, Testing Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft disc, seat material with Black Nitrile EPDM, flanges nuts and bots etc. |  | 0.00 | 0.00 |  | 0
166424 | B.2.1 | 40 mm Dia | Nos | 0.00 | 1.00 |  | 0
166425 | B.3 | Supply, Installation, Testing Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem lever, with necessary weldable fittings in position as per drawings site conditions. |  | 0.00 | 0.00 |  | 0
166426 | B.3.1 | 25 mm Dia | Nos | 0.00 | 1.00 |  | 0
166427 | B.4 | Supply, Installation, Testing Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor zone inside proposed demise area tap of point, shall be connected to fire alarm panel through cable. |  | 0.00 | 0.00 |  | 0
166428 | B.4.1 | 40 mm Dia | Nos | 0.00 | 1.00 |  | 0
166429 | B.5 | Supply, Installation, Testing Commissioning of Pressure Guage with a range of (0 - 300) PSI and 90mm dial size, near to flow switch with ball valves, siphon, fittings like unions colors reducer etc. |  | 0.00 | 0.00 |  | 0
166430 | B.5.1 | Pressure Gauge with 1 4 BSPT NPT connection | Nos | 0.00 | 1.00 |  | 0
166431 |  | FIRE SPRINKLER PIPING |  | 0.00 | 0.00 |  | 0
166432 | B.6 | Supply, Installation, Testing Commissioning of MS C Class Fire Sprinkler Pipe confirming to IS 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns) |  | 0.00 | 0.00 |  | 0
166433 | B.6.1 | 25 mm Dia | Mtr | 0.00 | 7.00 |  | 0
166434 | B.6.2 | 32 mm Dia | Mtr | 0.00 | 4.00 |  | 0
166435 | B.6.3 | 40 mm Dia | Mtr | 0.00 | 6.00 |  | 0
166436 | B.7 | Supply Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1 (25mm) BSPT NPT connection),Outlet Reducer (1 2 (15mm) BSPT NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc. |  | 0.00 | 0.00 |  | 0
166437 | B.7.1 | Assembly Length of (1500 mm) | Nos | 0.00 | 4.00 |  | 0