## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
150761 | 2 | INDIGENOUS WORK |  | 0.00 | 0.00 |  | 0
150762 | 2.1 | INSTALLATION OF VRF OUT-DOOR UNITS |  | 0.00 | 0.00 |  | 0
150763 |  | Installation, Charging, Testing and commissioning of VRF system with Environment friendly refrigerant gas for the below mentioned system. This shall include lifting, shifting and positioning of outdoor units, nitrogen leak testing, oil charging, vaccumisation etc., |  | 0.00 | 0.00 |  | 0
150764 | a | Refrigeration Capacity - 14 HP | Nos. | 0.00 | 1.00 |  | 49000
150765 | 2.2 | INSTALLATION OF VRF INDOOR UNITS |  | 0.00 | 0.00 |  | 0
150766 |  | Installation, Charging, Testing and commissioning of units complete with centrifugal blower, cooling coil with suitable rows, electronic expansion valves, high efficiency pre filter sections, drain pump etc as per specifications. |  | 0.00 | 0.00 |  | 0
150767 | 0 | 2542 CFM 6.4 TR | Nos. | 0.00 | 2.00 |  | 8500
150768 | 0 | 318 CFM 0.6 TR | Nos. | 0.00 | 1.00 |  | 2500
150769 | 2.3 | INSTALLATION OF CENTRALISED REMOTE CONTROLLER |  | 0.00 | 0.00 |  | 0
150770 |  | Installation, Charging, Testing and commissioning of of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs TFAs) and BMS compatible with ethernet Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on stop, the operation mode temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function central operation stop, demand control, emergency stop, central operation output, central alarm output. Controller shall however be suitable for future connectivity of indoor outdoor units also. |  | 0.00 | 0.00 |  | 0
150771 | a | Central Remote Controller | Nos. | 0.00 | 1.00 |  | 5000
150772 | 2.4 | VRF REFRIGERANT PIPING FITTING WITH INSULATION |  | 0.00 | 0.00 |  | 0
150773 |  | Supply, Installation, Testing and Commissioning of the refrigerant piping with nitrile rubber insulation in sleeve form.It should be selected for maximum working pressure of 624 psi for R – 410a refrigerant circuit and for maximum working pressure of 500psi in case of R407C refrigerant. The Ref. Piping shall be pressure tested at 1.5 times the working pressure. Copper pipes shall be made of phosphorus deoxidized seamless copper. Minimum thickness to be used for refrigerant piping shall be as follows The insulation( Nitrile rubber, class-O, self extinguishing, CFC free, thermal conductivity of not more than .035w Wm°K shall be 19 mm thick for suction piping liquid line. All Exposed Piping on the floor shall be enclosed in openable GI trays insulation should be with UV protection with mil cloth.The Ref. Piping shall be properly supported at every 1.5 m distance with stands and support linked with rubber as per specifications. | Rmt | 0.00 | 75.00 |  | 2350
150774 |  | Make Maxflow Mandev Heling |  | 0.00 | 0.00 |  | 0
150775 |  | Note Referiferant piping shall include liquid + gas pipe with all necessory fittings. Also, the size of the same shall be as per manufactured standard. |  | 0.00 | 0.00 |  | 0
150776 | 2.5 | GAS CHARGING |  | 0.00 | 0.00 |  | 0
150777 |  | Additional gas charging - Over and above standard Gas charging quantity | Kg | 0.00 | 15.00 |  | 1550
150778 | 2.6 | REFNET JOINTS |  | 0.00 | 0.00 |  | 0
150779 |  | SITC of Special Refrigerant T Y-joints for VRF units | Nos | 0.00 | 2.00 |  | 5500
150780 | 2.7 | POWER CABLING |  | 0.00 | 0.00 |  | 0
150781 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. (Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by Owners Consultants. (MCCB,s provided 5m from Outdoor unit). |  | 0.00 | 0.00 |  | 0
150782 |  | Make Polycab, KEI Finolex |  | 0.00 | 0.00 |  | 0
150783 | b | Suitable copper Armoured cable - from MCB Isolator to VRF ODU. | Rmt | 0.00 | 5.00 |  | 370
150784 | d | 8 SWG Copper Wire | Rmt | 0.00 | 10.00 |  | 320
150785 | 2.8 | COMMUNICATION CABLE |  | 0.00 | 0.00 |  | 0
150786 |  | SITC of the control cabling from Indoor to outdoor unit Outdoor unit to CRC BACnet for all the units with the necessary fittings. The cabling shall be of weather proof type as most of the cabling will have open exposure to atmosphere. The cabling shall be bundled properly and shall be neatly aligned with the Refrigerant piping. The cabling shall be well supported with G.I cable tray throughout the piping length. |  | 0.00 | 0.00 |  | 0
150787 |  | Make Polycab, KEI Finolex |  | 0.00 | 0.00 |  | 0
150788 | a | 1.5 sqmm 2 core | Rmt | 0.00 | 135.00 |  | 290
150789 | 2.9 | PERFORATED GI CABLE TRAYS |  | 0.00 | 0.00 |  | 0
150790 |  | Supplying Fixing of following sizes of Perforated GI cable tray duly painted of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. External Internal refrigerant piping shall be provided and laid on GI covered cable trays with cover. |  | 0.00 | 0.00 |  | 0
150791 | a | 150mm wide | Rmt | 0.00 | 25.00 |  | 650
150792 | b | 300mm wide | Rmt | 0.00 | 50.00 |  | 850
150793 | 2.10 | FRAMEWORK FOR VRF ODU |  | 0.00 | 0.00 |  | 0
150794 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of air cooled remote condenser in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. | Nos. | 0.00 | 1.00 |  | 10500
150795 | 2.11 | INSULATED CONDENSATE DRAIN PIPE |  | 0.00 | 0.00 |  | 0
150796 |  | SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe . |  | 0.00 | 0.00 |  | 0
150797 |  | Make Supreme, Prince, Astral |  | 0.00 | 0.00 |  | 0
150798 | a | 25 mm Dia | Rmt | 0.00 | 30.00 |  | 175
150799 | b | 32 mm Dia | Rmt | 0.00 | 20.00 |  | 185
150800 | 2.12 | Supply, installation of Cowl piece connection with bird screen for VRF Outdoor units | Nos | 0.00 | 1.00 |  | 10000
150801 | Note : | Quantities of refrigerant piping and cabling are based on the drawings with Indoor Outdoor units Locations shown and for the specified configuration. Vendor to confirm refrigerant piping and cabling quantities based on the system configuration being offered by them. |  | 0.00 | 0.00 |  | 0
150802 | 3 | VENTILATION SYSTEM |  | 0.00 | 0.00 |  | 0
150803 | 3.1 | KITCHEN EXHAUST FAN |  | 0.00 | 0.00 |  | 0
150804 |  | SITC of Cabinet type SISW Centrifugal Blower, Belt Direct Drive, Statically Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class H Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads Canvass Connection. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation). |  | 0.00 | 0.00 |  | 0
150805 |  | Make Kruger Nicotra Avantec |  | 0.00 | 0.00 |  | 0
150806 | a | 6600 CFM, 65mm ESP (Class H) | Nos. | 0.00 | 1.00 |  | 145000
150807 | 3.2 | KITCHEN DRY SCRUBBER |  | 0.00 | 0.00 |  | 0
150808 |  | SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units. |  | 0.00 | 0.00 |  | 0
150809 |  | Finishing - Power coated, Dark Blue |  | 0.00 | 0.00 |  | 0
150810 |  | Operating voltage - 220 Vac+ -10%, 50 Hz (Single phase) |  | 0.00 | 0.00 |  | 0
150811 |  | Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator |  | 0.00 | 0.00 |  | 0
150812 |  | Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test |  | 0.00 | 0.00 |  | 0
150813 |  | Particle Size - Collects particles as small as 0.01 microns |  | 0.00 | 0.00 |  | 0
150814 |  | Motor - Sealead ball bearings UL, single phase. |  | 0.00 | 0.00 |  | 0
150815 |  | Cell - Ionizing voltage - 12 KVdc |  | 0.00 | 0.00 |  | 0
150816 |  | Collector voltage - 6 KVdc |  | 0.00 | 0.00 |  | 0
150817 |  | One cell comprising of 9 ionizing wires and 25 collection plates |  | 0.00 | 0.00 |  | 0
150818 |  | Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function. |  | 0.00 | 0.00 |  | 0
150819 |  | Pre-filter - Aluminium mesh, washable Dry contact for BMS. |  | 0.00 | 0.00 |  | 0
150820 |  | Make Rydair Espair |  | 0.00 | 0.00 |  | 0
150821 |  | CFM - 6600 | Nos. | 0.00 | 1.00 |  | 255000
150822 | 3.2 | KITCHEN FRESH AIR FAN WITH AIRWASHER TYPE |  | 0.00 | 0.00 |  | 0
150823 |  | SITC of CELDEK FILL package type air cooling unit with minimum 90% saturation efficiency. Air cooling unit shall be factory assembled and complete with double skin casing 0.8mm Inner outer pre-coated GI sheets, DIDW forward curved fans with TEFC, sq. cage, induction motors 1440 RPM (IE-3) with IP-55 Protection. Suitable for operation on 415 ± 10% voltage, 50 Hz 3 phase AC supply, drive package including multi sheave pulleys and belts for fans and motors, 1.2mm thick tank pad section in SS Construction, vibration isolators, wire mesh pre-filters, 200 mm thick CELDEK FILL, 1HP Water Circulation Pump (1W+1S), internal PVC piping, valves and fittings, 4-bend PVC eliminator. MERV 8 G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. (Vendor to crosscheck static pressure calculation) |  | 0.00 | 0.00 |  | 0
150824 |  | Make Kruger Nicotra Avantec |  | 0.00 | 0.00 |  | 0
150825 | a | 5600 CFM, 50mm ESP (Class F) | Nos. | 0.00 | 1.00 |  | 135000
150826 | 3.3 | FRAMEWORK FOR FANS |  | 0.00 | 0.00 |  | 0
150827 |  | Supply, Fabrication and Installation of MS frame using channels angle iron sections as required for mounting of ventilation fans scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects Structural Engineers prior to commencement of fabrication. | Kg | 0.00 | 200.00 |  | 550
150828 |  | Note |  | 0.00 | 0.00 |  | 0
150829 | a. | Fan outlet velocity - 1600 FPM |  | 0.00 | 0.00 |  | 0
150830 | b. | All cabinet fans should have plenum section. |  | 0.00 | 0.00 |  | 0
150831 | c. | Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework. |  | 0.00 | 0.00 |  | 0
150832 | d. | Contractor shall submit static pressure calculation for all above units to Client Consultant. |  | 0.00 | 0.00 |  | 0
150833 | e. | Any change in motor HP or coil selection shall be made at no extra cost to client. |  | 0.00 | 0.00 |  | 0
150834 | f. | Fan efficiency shall be minimum 75% |  | 0.00 | 0.00 |  | 0
150835 | g. | The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  | 0.00 | 0.00 |  | 0
150836 | 4 | SHEET METAL WORKS |  | 0.00 | 0.00 |  | 0
150837 | 4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT |  | 0.00 | 0.00 |  | 0
150838 |  | Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications. |  | 0.00 | 0.00 |  | 0
150839 |  | GI Sheet Makes Tata, Jindal, SAIL, Ispat |  | 0.00 | 0.00 |  | 0
150840 |  | Make Rola Star, Zeco Ductofab |  | 0.00 | 0.00 |  | 0
150841 | a | 18 Gauge GI Sheet Metal Duct (Above 2251mm Plenum) | Sq.mtr | 0.00 | 10.00 |  | 3099
150842 | b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) For Kitchen Exhaust Works | Sq.mtr | 0.00 | 150.00 |  | 2750
150843 | c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 0.00 | 100.00 |  | 1780
150844 | d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 0.00 | 120.00 |  | 1540
150845 | 4.2 | EXTRUDED ALUMINIUM CEILING GRILLES |  | 0.00 | 0.00 |  | 0
150846 |  | Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. |  | 0.00 | 0.00 |  | 0
150847 |  | Make Cosmos, Air Master System Air |  | 0.00 | 0.00 |  | 0
150848 |  | Linear Square Rectangular Grille | Sq.mtr | 0.00 | 6.00 |  | 18500
150849 | 4.3 | SS EXHAUST AND FRESH AIR GRILLES |  | 0.00 | 0.00 |  | 0
150850 |  | SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature. |  | 0.00 | 0.00 |  | 0
150851 |  | Make Carryaire System Air Dynacraft Air Master |  | 0.00 | 0.00 |  | 0
150852 | a | Linear Square Rectangular Grille | Sq.mtr | 0.00 | 0.50 |  | 20500
150853 | 4.4 | DOOR TRANSFER GRILLE |  | 0.00 | 0.00 |  | 0
150854 |  | SITC of Aluminium extruded powder coated Door transfer grills. |  | 0.00 | 0.00 |  | 0
150855 |  | Door transfer grille (Back to Back) | Sq.mtr | 0.00 | 1.00 |  | 19500
150856 |  | Make Cosmos, Air Master System Air |  | 0.00 | 0.00 |  | 0
150857 | 4.5 | MULTI LEAF VOLUME CONTROL DAMPER |  | 0.00 | 0.00 |  | 0
150858 |  | SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 0.00 | 2.50 |  | 20500
150859 |  | Make Cosmos, Air Master System Air |  | 0.00 | 0.00 |  | 0
150860 | 4.6 | OPPOSED BLADE DAMPER |  | 0.00 | 0.00 |  | 0
150861 |  | SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 0.00 | 2.00 |  | 20500
150862 | 4.7 | CANVAS CONNECTION |  | 0.00 | 0.00 |  | 0
150863 |  | SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type). |  | 0.00 | 0.00 |  | 0
150864 | a | For VRF Ductable Unit | Nos. | 0.00 | 3.00 |  | 15500
150865 | c | For Kitchen EX FA Fan | Nos. | 0.00 | 4.00 |  | 15500
150866 | 4.8 | CURTAIN TYPE FIRE DAMPER |  | 0.00 | 0.00 |  | 0
150867 |  | SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 225°F, etc; as per the approved shop drawings and specifications. |  | 0.00 | 0.00 |  | 0
150868 |  | Make Carryaire System Air Dynacraft Air Master |  | 0.00 | 0.00 |  | 0
150869 | a | Bare fire dampers | Sq.mtr | 0.00 | 1.00 |  | 35500
150870 | b | Fusible link as per specification UL 555 | No | 0.00 | 1.00 |  | 35500
150871 |  | NOTES |  | 0.00 | 0.00 |  | 0
150872 |  | The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant. |  | 0.00 | 0.00 |  | 0
150873 |  | Muslin cloth cover for all air outlets during construction. |  | 0.00 | 0.00 |  | 0
150874 |  | Pressure testing of complete duct work as per DW SMACNA standard. |  | 0.00 | 0.00 |  | 0
150875 |  | Silicon sealant for longitudinal transverse joints as per specification. |  | 0.00 | 0.00 |  | 0
150876 |  | Diffusers grilles shall be powder coated as per color approved by Architect. |  | 0.00 | 0.00 |  | 0
150877 | 5 | THERMAL ACOUSTIC INSULATION |  | 0.00 | 0.00 |  | 0
150878 | 5.1 | THERMAL INSULATION |  | 0.00 | 0.00 |  | 0
150879 |  | Supply fixing of Thermal insulation for supply air duct using 19mm thick class O Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W (m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 0.00 | 100.00 |  | 1550
150880 |  | Make Armaflex K-flex Aerofoam ALP Aeroflex |  | 0.00 | 0.00 |  | 0
150881 | 5.2 | ACOUSTIC INSULATION |  | 0.00 | 0.00 |  | 0
150882 |  | Supply fixing acoustic insulation for ducting using Class 1 closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal transverse joints sealed with adhesive in neat clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W (m.K) and density of 140 - 180 kg m³. | Sq.mtr | 0.00 | 25.00 |  | 1350
150883 |  | Make Armaflex K-flex Aerofoam ALP Aeroflex |  | 0.00 | 0.00 |  | 0
150884 | 5.3 | THERMAL INSULATION FOR KITCHEN EXHAUST DUCTS |  | 0.00 | 0.00 |  | 0
150885 |  | SITC of 80mm thick Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 32 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. | Sq.mtr | 0.00 | 150.00 |  | 1650
150886 |  | Make Rockwool UP Twiga |  | 0.00 | 0.00 |  | 0
150887 |  | Note |  | 0.00 | 0.00 |  | 0
150888 | a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement. |  | 0.00 | 0.00 |  | 0
150889 | b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition. |  | 0.00 | 0.00 |  | 0
150890 | c. | Thermal insulation shall be internal for Elliptical Expossed ducting. |  | 0.00 | 0.00 |  | 0
150891 | 6 | ELECTRICAL WORKS |  | 0.00 | 0.00 |  | 0
150892 | 6.2 | POWER CABLING |  | 0.00 | 0.00 |  | 0
150893 |  | Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. |  | 0.00 | 0.00 |  | 0
150894 | a | Suitable Power Cable |  | 0.00 | 0.00 |  | 0
150895 |  | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Rmt | 0.00 | 10.00 |  | 750
150896 |  | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Rmt | 0.00 | 10.00 |  | 750
150897 | b | Earthing |  | 0.00 | 0.00 |  | 0
150898 |  | 8 SWG | Rmt | 0.00 | 40.00 |  | 850
150899 | 6.3 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
150900 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. |  | 0.00 | 0.00 |  | 0
150901 | a | Suitable for 6600 CFM Kitchen Exhaust Fan, Star Delta Panel with VFD | Nos. | 0.00 | 2.00 |  | 15500
150902 | b | Suitable for 5600 CFM Kitchen Air-washer, Star Delta Panel with VFD | Nos. | 0.00 | 2.00 |  | 16500
150903 | 6.4 | CABLE TRAYS |  | 0.00 | 0.00 |  | 0
150904 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. |  | 0.00 | 0.00 |  | 0
150905 | a | 50mm wide x 50mm ht x 1.6mm thick | Rmt | 0.00 | 20.00 |  | 1250