## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
176438 | C | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE ) |  | 0.00 | 0.00 |  | 0
176439 |  | FIRE ALARM SYSTEM - DETECTION DEVICES |  | 0.00 | 0.00 |  | 0
176440 | C.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles with all necessary mounting and fixing arrangements. (Above Below Ceiling) |  | 0.00 | 0.00 |  | 0
176441 | C.1.1 | Below ceiling level | Nos | 0.00 | 2.00 |  | 7200
176442 | C.1.2 | Above ceiling level | Nos | 0.00 | 2.00 |  | 7500
176443 | C.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements. |  | 0.00 | 0.00 |  | 0
176444 | C.2.1 | Heat Detector - 58°C fixed temperature | Nos | 0.00 | 1.00 |  | 7810
176445 | C.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. |  | 0.00 | 0.00 |  | 0
176446 | C.3.1 | Manual Call Point - (Wall Partition Mounted) | Nos | 0.00 | 1.00 |  | 6945
176447 | C.4 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements. |  | 0.00 | 0.00 |  | 0
176448 | C.4.1 | Response Indicator Remote Indicator | Nos | 0.00 | 2.00 |  | 1250
176449 |  | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES |  | 0.00 | 0.00 |  | 0
176450 | C.5 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles. |  | 0.00 | 0.00 |  | 0
176451 | C.5.1 | Sounder Strobe - (Wall Partition Mounted) | Nos | 0.00 | 1.00 |  | 10200
176452 |  | FIRE ALARM SYSTEM - MODULE DEVICES |  | 0.00 | 0.00 |  | 0
176453 | C.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. |  | 0.00 | 0.00 |  | 0
176454 | C.6.1 | Isolator Module | Nos | 0.00 | 1.00 |  | 6450
176455 |  | FIRE ALARM SYSTEM - CABLING |  | 0.00 | 0.00 |  | 0
176456 | C.7 | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements. |  | 0.00 | 0.00 |  | 0
176457 | C.7.1 | 2C x 1.5 Sq. mm Cu Cable | Mtr | 0.00 | 45.00 |  | 170