## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
167534 | B | DRAINAGE VENT SYSTEMS |  | 0.00 | 0.00 |  | 0
167535 |  | DRAINAGE EQUIPMENTS |  | 0.00 | 0.00 |  | 0
167536 | B.1 | Supply, Installation and Testing of Grease Trap (Above Ground floor) of approved make of 304-grade stainless steel material with interceptor body, perforated bucket, baffles, integral trap, inlet, and outlet pipe sleeve, and stainless steel interceptor cover with all necessary fittings connectors, etc. |  | 0.00 | 0.00 |  | 0
167537 | B.1.1 | 8 GPM - Flow Rate (0.50 LPS 30.28 LPM) | Nos | 0.00 | 2.00 |  | 0
167538 |  | VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
167539 | B.2 | Supply, Installation and Testing of Air Admittance Valve of approved make conforming to EN 12380, with an air admittance air flow rate of 6.1 LPS and a temperature range of operation from -20 °C to + 60 °C with all necessary adapters, fittings and connectors etc. |  | 0.00 | 0.00 |  | 0
167540 | B.2.1 | 32 mm Dia | Nos | 0.00 | 2.00 |  | 0
167541 |  | DRAINS, TRAPS CLEANOUTS |  | 0.00 | 0.00 |  | 0
167542 | B.3 | Supply, Installation and Testing of AISI 304 grade Stainless Steel Floor Drain of approved make with top square anti-slip mesh grating drain cover of 300 X 300 mm, lateral horizontal outlet, with removable waste basket, odor water seal trap with all necessary adapters, fittings and connectors etc. |  | 0.00 | 0.00 |  | 0
167543 | B.3.1 | 50 mm Dia - Outlet | Nos | 0.00 | 2.00 |  | 0
167544 | B.4 | Supply, Installation and Testing of uPVC Multi Floor Trap of approved make with stainless steel slotted top cover, flap, and air-tight cleaning eye, odor water seal trap with all necessary adapters, fittings, and connectors, etc. |  | 0.00 | 0.00 |  | 0
167545 | B.4.1 | ( 3 Nos X 50 mm Dia - Inlet ) 75 mm Dia - Outlet | Nos | 0.00 | 1.00 |  | 0
167546 | B.5 | Supply, Installation and Testing of of uPVC P Trap (self-cleaning type) of approved make with odor water seal trap with all necessary adapters, fittings and connectors, etc. |  | 0.00 | 0.00 |  | 0
167547 | B.5.1 | 40 mm Dia - Outlet | Nos | 0.00 | 3.00 |  | 0
167548 |  | DRAINAGE VENT SYSTEMS PIPING |  | 0.00 | 0.00 |  | 0
167549 | B.6 | Supply, Installation and Testing of of uPVC Pipe of approved make conforming to IS 13592, for drainage with all necessary fittings such as bends, wye s, reducers, san tee s, double wye s, double combinations, san cross, and cleanout plugs etc, with all necessary supports clamps for the above-raised floor pipes as per standards and site conditions requirements. |  | 0.00 | 0.00 |  | 0
167550 | B.6.1 | 32 mm Dia | Nos | 0.00 | 2.00 |  | 0
167551 | B.6.2 | 40 mm Dia | Nos | 0.00 | 5.00 |  | 0
167552 | B.6.3 | 50 mm Dia | Nos | 0.00 | 17.00 |  | 0
167553 | B.6.4 | 75 mm Dia | Nos | 0.00 | 2.00 |  | 0
167554 |  | TESTING COMMISSIONING |  | 0.00 | 0.00 |  | 0
167555 | B.8 | Water Air Test for Drainage and Vent system pipes for leak detection |  | 0.00 | 0.00 |  | 0
167556 | B.8.1 | The drainage and vent system shall be water air tested with all openings in the piping tightly closed, except the highest opening to detect any water leakage in the system. The test is to be conducted after the complete installation of all drainage and vent system pipes and accessories as per the proposed design. | Set | 0.00 | 1.00 |  | 0
167557 | C | WATER SUPPLY SYSTEM |  | 0.00 | 0.00 |  | 0
167558 |  | WATER SUPPLY EQUIPMENTS |  | 0.00 | 0.00 |  | 0
167559 | C.1 | Supply, Installation, Testing, and commissioning of Electric Water Heater of approved make with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. The unit shall be suitable for 230 ± 10 volts, 50 60 Hz, 1 phase AC supply and proper supports necessary as per standards and site condition requirements. |  | 0.00 | 0.00 |  | 0
167560 | C.1.1 | 40 Litres vertical storage water heater | Nos | 0.00 | 1.00 |  | 0
167561 | C.2 | Supply, Installation, Testing of Multi-Jet water meter of approved make conforming to IS 779 94 and Class B of ISO 4064, with Brass body and coupling, hermetically sealed water meter with magnetically driven totalizer, sealed against tampering, leakproof having dry dial, etc. and shall be operated with a working condition of water temperature upto 50°C and a Maximum pressure of 16 Bar( with BMS integration ). |  | 0.00 | 0.00 |  | 0
167562 | C.2.1 | 25 mm Dia | Nos | 0.00 | 1.00 |  | 0
167563 | C.3 | Supply, Installation, Testing, and commissioning of RO Filter with inbuild pump of approved make of compact size for supplying pure filtered potable water to equipment like Combi-steamers and baking ovens, Fresh water taps and coolers, Coffee Espresso machines, Post-mix machines, Ice-machines, and Boiling-water taps etc. with Indicating panel, Dust proof cover, filter cartridges, Pressure pump, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. The final make, model, and details are to be finalized by the specialist vendor after examining the water test report of the incoming water supply provided at the site. |  | 0.00 | 0.00 |  | 0
167564 | C.3.1 | 1.5 Ltrs Min - Flow Rate | Nos | 0.00 | 1.00 |  | 0
167565 |  | TAPS |  | 0.00 | 0.00 |  | 0
167566 | C.4 | Supply, Installation, Testing, and Commissioning of chrome plated Mixer Tap with Flexible hose connector, Pillar tap fixing studs, Washer etc.. with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall partition as per Architectural Interior Design and as per relevant standards.(Model as per Equipment ventor ID Design Architectural design) |  | 0.00 | 0.00 |  | 0
167567 | C.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp fixture connection) | Nos | 0.00 | 3.00 |  | 0
167568 |  | WATER SUPPLY PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
167569 | C.6 | Supply, Installation and Testing of Brass Ball Valve of approved make with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar with all necessary fittings. |  | 0.00 | 0.00 |  | 0
167570 | C.6.1 | 25 mm Dia | Nos | 0.00 | 3.00 |  | 0
167571 | C.7 | Supply, Installation and Testing of chrome plated Angle Valve of approved make with wall flange rosette for all plumbing equipment fixtures with a pressure rating of 16 Bar with all necessary fittings. Including making good the wall partition as per Architectural Interior Design and as per relevant standards. |  | 0.00 | 0.00 |  | 0
167572 | C.7.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp fixture connection) | Nos | 0.00 | 8.00 |  | 0
167573 | C.7.2 | 20 mm Dia Inlet (Outlet size to fit with plumbing eqp fixture connection) | Nos | 0.00 | 4.00 |  | 0
167574 | C.8 | Supply, Installation and Testing of Water Hammer Arrester of approved make with Factory air charged and permanently sealed for an Air pre-load of 4.2 Bar, Designed to operate at a working pressure of 10.6 Bar, and temperature range of 0.5°C to 82°C with all necessary fittings connectors etc. |  | 0.00 | 0.00 |  | 0
167575 | C.14.1 | 25 mm Inlet Dia | Nos | 0.00 | 1.00 |  | 0
167576 |  | COLD WATER SUPPLY PIPING |  | 0.00 | 0.00 |  | 0
167577 | C.9 | Supply, Installation and Testing of (Chlorinated Poly Vinyl Chloride) CPVC Pipe of approved make conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions, etc, and proper supports were necessary as per standards and site condition requirements. |  | 0.00 | 0.00 |  | 0
167578 | C.9.1 | 15 mm Dia | Mtr | 0.00 | 5.00 |  | 0
167579 | C.9.2 | 20 mm Dia | Mtr | 0.00 | 10.00 |  | 0
167580 | C.9.3 | 25 mm Dia | Mtr | 0.00 | 12.00 |  | 0
167581 |  | HOT WATER SUPPLY RETURN PIPING |  | 0.00 | 0.00 |  | 0
167582 | C.10 | Supply, Installation and Testing of (Chlorinated Poly Vinyl Chloride) CPVC Pipe of approved make conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 85°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions, etc, and proper supports were necessary as per standards and site condition requirements. |  | 0.00 | 0.00 |  | 0
167583 | C.10.1 | 15 mm Dia | Mtr | 0.00 | 4.00 |  | 0
167584 | C.10.2 | 20 mm Dia | Mtr | 0.00 | 5.00 |  | 0
167585 |  | PIPING THERMAL INSULATION |  | 0.00 | 0.00 |  | 0
167586 | C.11 | Supply and fixing of Pipe Insulation of 9 mm thick, with closed cell flexible elastomeric foam made from Nitrile rubber with 26-gauge Aluminium cladding of approved make to prevent external mechanical damage of approved make for Hot water pipe with an operating temperature range of -40°C to +105°C, Thermal conductivity (?) 0.040 W m-K @ 40°C including suitable adhesives to fix the insulation to pipe. |  | 0.00 | 0.00 |  | 0
167587 | C.11.1 | For 15 mm Pipe Dia | Mtr | 0.00 | 4.00 |  | 0
167588 | C.11.2 | For 20 mm Pipe Dia | Mtr | 0.00 | 5.00 |  | 0
167589 | D | PLUMBING SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
167590 | D.1 | All services for pipes Like Type of water, pipe size, Flow direction need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
167591 | D.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 0
167592 | E | TESTING COMMISSIONING |  | 0.00 | 0.00 |  | 0
167593 | E.1 | Water Quality Analysis Report |  | 0.00 | 0.00 |  | 0
167594 | E.1.1 | Supplied incoming water samples are to be tested for pH value, Conductivity, TDS, Total Hardness, Mineral contents, Total Chlorine, Bacteria presence, color, odor, etc. to identify whether the supplied water is suitable for drinking purposes and also to finalize the selection design of water filtration treatment system. The test analysis is to be conducted before any construction related to the water supply system at the site. | Set | 0.00 | 1.00 |  | 0
167595 | E.2 | Incoming water supply tap-off point water pressure and flow test |  | 0.00 | 0.00 |  | 0
167596 | E.2.1 | Incoming water supply tap-off point water pressure is to be tested at the site to identify whether the water supply has sufficient pressure and flow to serve the remote end plumbing fixture equipment with minimum flow pressure requirement to the fixture. (The proposed water supply design is based on the assumption that the supplied water has enough pressure and flow to serve the plumbing fixtures equipment). The test is to be conducted prior to any construction related to the water supply system at the site. | Set | 0.00 | 1.00 |  | 0
167597 | E.3 | Pressure test for Water supply system pipes for leak detection |  | 0.00 | 0.00 |  | 0
167598 | E.3.1 | Water supply system pipes are to be pressure tested at the site with a Test pressure Head of 10 Bar for a duration of 24 Hours to detect any water leakage in the system. The test is to be conducted after the complete installation of all water supply system pipes and accessories as per the proposed design. | Set | 0.00 | 1.00 |  | 0