## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
71615 |  | 18 G sheet | sq.m | 0.00 | 25.00 |  | 2420
71621 |  | 18 G sheet | sq.m | 0.00 | 5.00 |  | 2000
71626 | 4 | Supplying fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 0.00 | 1.00 |  | 10500
71639 |  | The panel shall include the following components and accessories. |  | 0.00 | 0.00 |  | 0
71624 |  | 24G sheet | sq.m | 0.00 | 5.00 |  | 1155
71628 | 6 | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.00 | 0.00 |  | 0
71646 | g. | Time delay relay for delayed automatic restart of air handling unit motor. |  | 0.00 | 0.00 |  | 0
71634 | D | ELECTRICAL INSTALLATION |  | 0.00 | 0.00 |  | 0
71635 | 1 | CONTROL PANEL FOR AHU Air washer Scrubber (WITH DOL SD STARTER) |  | 0.00 | 0.00 |  | 0
71636 |  | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing terminating into MCCB in each panel shall be provided by the electrical contractor. |  | 0.00 | 0.00 |  | 0
71619 |  | 26G sheet | sq.m | 0.00 | 5.00 |  | 1330
71620 | 2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required |  | 0.00 | 0.00 |  | 0
71612 | B | AIR DISTRIBUTION |  | 0.00 | 0.00 |  | 0
71630 | C | THERMAL INSULATION |  | 0.00 | 0.00 |  | 0
71645 | f. | Digital voltmeter and digital ammeter with selector switches. |  | 0.00 | 0.00 |  | 0
71633 |  | 13 mm Thick | sq.m | 0.00 | 30.00 |  | 850
71614 | 1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support. |  | 0.00 | 0.00 |  | 0
71640 | a. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA. |  | 0.00 | 0.00 |  | 0
71616 |  | 20G sheet | sq.m | 0.00 | 5.00 |  | 2000
71644 | e. | Phase indicating lights and indicating light for ON status. |  | 0.00 | 0.00 |  | 0
71623 |  | 22G sheet | sq.m | 0.00 | 5.00 |  | 1350
71625 | 3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.00 | 1.00 |  | 13000
71627 | 5 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 0.00 | 2.00 |  | 1500
71613 |  | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS SPECIFICTIONS) |  | 0.00 | 0.00 |  | 0
71629 | 7 | Supply, installation, testing and balancing of Powder coated Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | SQMT | 0.00 | 0.00 |  | 0
71632 |  | SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. |  | 0.00 | 0.00 |  | 0
71641 | b. | DOL SD starter as per HP ratings |  | 0.00 | 0.00 |  | 0
71647 | h | For on off remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. |  | 0.00 | 0.00 |  | 0
71642 | c. | Terminal block for power distribution. |  | 0.00 | 0.00 |  | 0
71643 | d. | Contactor, over load relay with built in single phasing protection. |  | 0.00 | 0.00 |  | 0
71648 | i | All starters shall be provided with suitable potential free contract for connections to the Building Automation System. |  | 0.00 | 0.00 |  | 0
71650 |  | 3 HP DOL Starter | No. | 0.00 | 1.00 |  | 16000
71637 |  | All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included. |  | 0.00 | 0.00 |  | 0
71649 |  | The number of AHU control panels shall be as follows. |  | 0.00 | 0.00 |  | 0
71617 |  | 22G sheet | sq.m | 0.00 | 5.00 |  | 1725
71618 |  | 24G sheet | sq.m | 0.00 | 40.00 |  | 1500
71622 |  | 20G sheet | sq.m | 0.00 | 5.00 |  | 1625
71631 | 1 | THERMAL INSULATION FOR KITCHEN DUCTS |  | 0.00 | 0.00 |  | 0
71651 |  | 5 HP DOL Starter | No. | 0.00 | 1.00 |  | 20000
71638 |  | All outgoing shall be provided with Stop Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. |  | 0.00 | 0.00 |  | 0