## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
174624 | 1.0 | PANELS DBsSupply and Installation of main LT panel,genarally conforming to IS 8623 IS-13947 IEC-439 front operated, dead back floor mounted , totally enclosed, compartmentalised, vermin proof,indoor, non-drawout type,power panel, fabricated out of 2 1.6mm thick CRCA sheets, fully powder coated after seven tank treatment, having gasketed hinged cover on each cubicle with insulated door knob, incorporating horizontal and vertical copper busbars complete with all internal wiring, danger sign board, earth-bus and lugs, cable chamber, busbar chamber,aluminium anodized name plates etc.as required, including 2 nos. of 6 dia instrument cooling fan with switch and ventilation louvres with wire mesh,housing below mentioned switchgears meters. 9W fitting with CFL lamp, switch shall be provided in each vertical section, (Panel should conform to Form- 3b of IEC- 439) (GA drawing of the panel to be got approved from the Consultant before taking up fabrication and all panels to be factory inspected before despatch) Notes 1. All MCCBs shall have rotary handle 2. All MCCBs shall have phase spreader assembly onboth Line Load ends. 3. All MCCB shall have Minimum Ics=Icu4. Incomer shall have auxilliary ON OFF TRIP status contacts and the same shall be wired upelectronic trip setting to Metering Compartment)5. The panel shall conform to Form-3b as per IEC-4396. All MCCB to be of Schneider ABB make7. All MCCB to be current limiting type, LSIG 8. Incomer MCCB to be shunt trip facilityRefer SLD |  | 0.00 | 0.00 |  | 0
174625 | 1.2 | Suply and installation of Four -Tier, Multi-Way, TPN, Distribution Board for Lighting Power distribution, surface mounted on wall, sheet metal fabricated,powder coated, having dust-proof and vermin proof, gasketed and hinged acrylic door with all internals such as DIN rails, neutral-link, interconnected wiring complete with earthing lugs housing switchgears (IP-43 with Metal Door) Refer SLD DB Schedule (Make Legrand-Ekinoxe Schneider) |  | 0.00 | 0.00 |  | 0
174626 | 1.2.2 | VTPN DB (6WAY TPN) | Set | 0.00 | 1.00 |  | 0
174627 | 1.2.3 | LPDB 1 (2+8WAY TPN) | Set | 0.00 | 1.00 |  | 0
174628 | 1.2.4 | UPSDB (8WAY SPN) | Set | 0.00 | 1.00 |  | 0
174629 | 1.6 | S I of 40A, TP, MCB + 415 V, in powder coated sheet metal box for terminating UPS to UPS DB etc. | Nos | 0.00 | 2.00 |  | 0
174630 | 1.8 | S I of 32A,TP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Set | 0.00 | 4.00 |  | 0
174631 | 2.0 | CABLES |  | 0.00 | 0.00 |  | 0
174632 | 2.1 | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE armoured unarmoured GI insulated GI sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts laid in ground laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications. |  | 0.00 | 0.00 |  | 0
174633 | 2.1.6 | 3.5C x 25 Sq.mm. CU Cable | R.M | 0.00 | 80.00 |  | 0
174634 | 2.1.7 | 4C x 16 Sq.mm. CU Cable | R.M | 0.00 | 60.00 |  | 0
174635 | 2.1.8 | 4C x 10 Sq.mm. CU Cable | R.M | 0.00 | 20.00 |  | 0
174636 | 2.1.11 | 4C x 2.5 Sq.mm. CU Cable | R.M | 0.00 | 40.00 |  | 0
174637 | 2.1.15 | 3C X 4sq.mm CU Cable - UPS, UPS DB | R.M | 0.00 | 60.00 |  | 0
174638 | 2.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
174639 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
174640 | 2.2.6 | 3.5C x 25 Sq.mm. CU Cable - VTPN DB | Nos. | 0.00 | 2.00 |  | 0
174641 | 2.2.7 | 4C x 16 Sq.mm. CU Cable | Nos. | 0.00 | 2.00 |  | 0
174642 | 2.2.15 | 3C X 4sq.mm CU Cable - UPS, UPS DB | Nos. | 0.00 | 2.00 |  | 0
174643 | 3.0 | POINT WIRING LIGHT POINT Sub mains Pre-Primary wiring i.e. from DB to room switch board shall be carried out for Pre-primary point using 2.5 sqmm copper stranded. All lighting fixture, wiring shall be carried out for primary point using 2.5 sqmm copper stranded for secondary wiring 1.5sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduits (including flexible conduits for drops to light fittings) . Individual junction inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12-8 points 800 watts as per following configuration (LDBs located at two locations as shown) (The Switch Socket cost shall be paid separately.)From distribution board to switch board will be termed as Pre-primary point, average wiring length for Pre-primary point to be considered as 20 metres. From switch board to first light fitting and switch board to switch board will be termed as primary point, average wiring length for primary point to be considered as 6 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 4 metres. Light point wiring shall be included submains wiring from D.B. to room switch board. Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
174644 | 3.1.2 | Primary point | Nos | 0.00 | 4.00 |  | 0
174645 | 3.1.3 | Secondary Point | Nos | 0.00 | 20.00 |  | 0
174646 | 3.4 | Power Point (Kitchen BAR)Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 4 sqmm copper stranded. Also used 3R x 2.5sqmm copper stranded. Secondary wiring 4 sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduit . Individual junction inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 22 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 1 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point. Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
174647 | 3.4.1 | Primary point | Nos | 0.00 | 10.00 |  | 0
174648 | 3.5 | S I of GI conduits including all accessories, clamps, spacers, bends, tee, cross etc. as required at site for miscellaneous use in following sizes |  | 0.00 | 0.00 |  | 0
174649 | 3.5.2 | 25mm dia | Mtr | 0.00 | 120.00 |  | 0
174650 | 3.6 | S I of flexible GI conduits including all accessories, clamps, spacers, end adopters (Glands) etc. as required at site in following sizes |  | 0.00 | 0.00 |  | 0
174651 | 3.6.2 | 25mm dia (COMMON) | Mtr | 0.00 | 140.00 |  | 0
174652 | 3.7 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular shuttered type switch socket outlets with modular front plate, on Suitable MS box, G.I. back box and all required accessories etc. Supply Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw wall plugs and other necessary hardware, marking identification numbers of circuits interconnections of the switch sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND |  | 0.00 | 0.00 |  | 0
174653 | 3.7.1 | POS COUNTER | Nos. | 0.00 | 1.00 |  | 0
174654 | 3.7.2 | Cold Display Counter | Nos. | 0.00 | 1.00 |  | 0
174655 | 3.7.3 | Coffee Machine | Nos. | 0.00 | 1.00 |  | 0
174656 | 3.7.4 | Milk Fridge | Nos. | 0.00 | 1.00 |  | 0
174657 | 3.7.5 | High Speed Oven | Nos. | 0.00 | 1.00 |  | 0
174658 | 3.7.6 | Sandwich Griller | Nos. | 0.00 | 2.00 |  | 0
174659 | 3.7.8 | Microwave Oven | Nos. | 0.00 | 1.00 |  | 0
174660 | 3.7.21 | data cum telephone back GI BACK box 2”x2” suitable for data socket | Nos. | 0.00 | 2.00 |  | 0
174661 | 3.7.24 | USB Point | Nos. | 0.00 | 4.00 |  | 0
174662 | 4.4 | S I of 1 Run x 25mm dia, Conduit in Floor. | Mtr | 0.00 | 80.00 |  | 0
174663 | 4.7 | S I of floor junction boxes similar to above but size 150mm x 150mm x 60 mm | Nos | 0.00 | 2.00 |  | 0
174664 | 4.8 | S I of GI Pregalvanizd Perforated type Cable Tayof following sizes suspended from ceiling or fixedvertically on wall column as per route directed at site including all necessary bends, tees, crosses and alsoincluding all necessary supporting arrangement.All supporting hardware including nuts, bolts etc. shall be also of galvanised M.S. as approved(PROFAB INDIANA ASIAN approved equivalent) |  | 0.00 | 0.00 |  | 0
174665 | 4.8.1 | 100mm x 50mm x 1.6mm | Mtr | 0.00 | 15.00 |  | 0
174666 | 5.0 | LIGHT FIXTURES INSTALLATION |  | 0.00 | 0.00 |  | 0
174667 | 5.1 | Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect consultant at site. |  | 0.00 | 0.00 |  | 0
174668 | 5.1.1 | FILAMENT BULB | Mtr | 0.00 | 20.00 |  | 0
174669 | 5.1.2 | TRACK LIGHT ( 1000 MM ) | Nos | 0.00 | 2.00 |  | 0
174670 | 5.1.3 | TRACK LIGHT ( 600 MM ) | Nos | 0.00 | 2.00 |  | 0
174671 | 5.1.9 | SINGNAGE | Nos | 0.00 | 2.00 |  | 0
174672 | 6.0 | EARTHING |  | 0.00 | 0.00 |  | 0
174673 | 6.3 | 8 SWG GI bare wire | Mtr | 0.00 | 60.00 |  | 0
174674 | 6.4 | 8 SWG CU bare wire | Mtr | 0.00 | 50.00 |  | 0
174675 | 6.5 | 25mm x 3mm thick GI strip welded painted green | Mtr | 0.00 | 72.00 |  | 0
174676 | 6.7 | S I of isolated dedicated earthing grounding system for computers etc.using insulated green-yellow copper earthing wire laid fixed bare on wall ceiling from separately made earth pit to the equipment in following sizes The rate shall include termination also. |  | 0.00 | 0.00 |  | 0
174677 | 7 | Miscellaneous Item |  | 0.00 | 0.00 |  | 0
174678 | 7.1 | Supply Install. Of RG 6 TV Cable in 25mm GIConduit | Mtr. | 0.00 | 40.00 |  | 0
174679 | 7.2 | Supply Laying of RG11 use for Main Cable TV | Mtr. | 0.00 | 50.00 |  | 0
174680 | 7.3 | Install. Of TV Stand - Only Installation | Nos. | 0.00 | 1.00 |  | 0
174681 | 8 | DATA DISTRIBUTION |  | 0.00 | 0.00 |  | 0
174682 |  | Supply, Installation, termination testing of data system |  | 0.00 | 0.00 |  | 0
174683 | 8.1 | Main SERVER ROUTER | Nos. | 0.00 | 1.00 |  | 0
174684 | 8.2 | SMART GIGABIT SWITCH 16 PORTS | Nos. | 0.00 | 1.00 |  | 0
174685 | 8.3 | Loaded PATCH PANEL for 16 Port | Nos. | 0.00 | 1.00 |  | 0
174686 | 8.4 | LIU switch with Accessories. (Optional if Fibre Optic Cable terminated) | Job | 0.00 | 1.00 |  | 0
174687 | 8.5 | Supply Installation of I O DATA Outlet (RJ-45) | Nos. | 0.00 | 13.00 |  | 0
174688 | 8.6 | S I of Installation of Wi-Fi ceiling mounted Access Point, managed by controller software | Nos. | 0.00 | 1.00 |  | 0
174689 | 8.8 | CABLES |  | 0.00 | 0.00 |  | 0
174690 | 8.8.3 | Supply providing of CAT 6 UTP cables in the laid raceways Conduits including terminations | Mtr. | 0.00 | 264.00 |  | 0
174691 | 8.8.4 | Patch cord (2 mtr-user end) | Each | 0.00 | 13.00 |  | 0
174692 | 8.9 | Supply, Installation, Testing Commissioning of Velcro Ties ( 22 Mtrs = 1 Roll) | Roll | 0.00 | 1.00 |  | 0
174693 | 8.10. | Supply, Installation, Testing Commissioning of Cable Ties 200mm ( 100 Nos. Pkt) | Pkt. | 0.00 | 1.00 |  | 0
174694 | 8.11 | Project Management including Freight Forwarding, Cable Bunching, Printed Numbering, tube type Ferruling both sides, Face plate, Patch panel patch cords both sides, Documentation etc.. | Job | 0.00 | 1.00 |  | 0
174695 | 8.12 | Supplying and fixing 4U Rack Aluminium Frame - 500x500mm with 2 x FAN, Dual Split perforated Door at Front and Back Side, 2 x Vertical Cable Basket, 2 x 12 socket 5 15A PDU with MCB, side Panels of 2 nos and Heavy Duty Castors with break, 19 Reduced Channel - Loop Type (DATA+CCTV) | Job | 0.00 | 1.00 |  | 0
174696 | 9.0 | SUPPLY INSTALLATION OF SAFETY ITEMS |  | 0.00 | 0.00 |  | 0
174697 | 9.3 | Caution boards (415V) of std. Size | Nos | 0.00 | 1.00 |  | 0
174698 | 9.4 | Rubber mat at panel room 12mm thk. 1mtr. Wide | Mtrs | 0.00 | 1.00 |  | 0
174699 | 9.5 | Shock treatment chart as per electricity board | Nos | 0.00 | 1.00 |  | 0
174700 | 10.0 | UPS INVERTER System |  | 0.00 | 0.00 |  | 0
174701 | 10.1 | Supply, Installation, testing and commissioning of 2 KVA UPS System Single Phase I C Single Phase O G complete with in Built Battery, 30 Minutes Battery Back-up the required accessories as specified in the drawings the specifications. Make Emerson APC Consul Neowatt Vivtar Electronics | set | 0.00 | 1.00 |  | 0