## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
117087 |  | General Notes for Electrical Work All materials and workman ship shall be to standards or consultants approval and shall comply with Local electrical rules Electrical Inspectorate. Color conduits should be used for data, raw power, UPS access control as listed below coding a) Raw Power and Lighting - Blue b) UPS - Black c) Data - Gray All Civil work for the electrical work such as Chipping or Cutting or Drilling and making good of Partition walls , False floor,Ceiling etc. as applicable shall be deemed included in scope of works |  | 0.00 | 0.00 |  | 0
117088 |  | MV Cables Copper Cables Supply installation of following LT XLPE FRLS cables rated for 600 or 1100 volts AC as per IS standard 1554 Part 1 IS standard 7098 Part 2, with necessary M.S. clamps. The cables shall be laid through partition walls, under false flooring, pipes etc. as required and shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 10 mtrs and ten finally with metal identification tags showing the size and the location from or to the specific Panel or DB at both ends. 4C x 25 Sq. mm A2XFY | M | 0.00 | 10.00 |  | 0
117089 |  | PVC Cable End Termination - Providing and termination for Armoured type copper cables with single compression brass glands, solderless tinned Cu crimping type lugs, gland earthing etc. complete 4C x 25 Sq. mm A2XFY | Nos. | 0.00 | 2.00 |  | 0
117090 |  | DISTRIBUTION BOARDS - Supply, installation, testing commissioning of Distribution Boards surface or flush mounted with double door containing MCB or ELMCB as incomer and SPMCB as outgoing. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate with knock-outs at the top bottom. All MCBs are of 10KA breaking capacity and ELMCBs or RCCB should be of 30mA or 100 or 300 mA sensitivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with feruling, dressing and all circuits shall be properly labelled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be D type and other MCBs shall be C category for lighting and raw power DB. 8way VTPN MCCB DB similar to Schneider MGNV10DD or AD4 with 100A TP+N MCCB as incomer, and 15 Nos. 10 or 16 or 25A SP C curve MCB as outgoings and 2nos. 4P or TP -32A MCB as outgoing as per SLD drawing. | Nos. | 0.00 | 1.00 |  | 0
117091 |  | CIRCUIT MAINS - Supply installation of 25 mm dia. HMS FRLS PVC conduits (Rigid or flexible), concealed with partition wall, storage units etc.; with necessary accessories (e.g. PVC bends, tees, pull box or junction box etc.) for power wiring as per design or layout. The rate shall include grooving through walls and providing MS brackets if required for any conduit suspension. |  | 0.00 | 0.00 |  | 0
117092 |  | - do - but conduit pipe shall be Rigid type. | M | 0.00 | 25.00 |  | 0
117093 |  | - do - but flexible conduit pipe | M | 0.00 | 10.00 |  | 0
117094 |  | Supply and laying of sub or circuit mains, using PVC insulated copper conductor of 1100 volt grade stranded flexible FRLS wire in prelaid FRLS PVC or GI conduit concealed or surface mounted making connections where ever required to complete the installation. Circuit mains shall be measured from DB to switch board and looping from switch board to switch board. |  | 0.00 | 0.00 |  | 0
117095 |  | 2R x 4.0 Sqmm + 1R x 2.5 Sqmm Cu. Wires | M | 0.00 | 60.00 |  | 0
117096 |  | 2R x 2.5 Sqmm + 1R x 1.5 Sqmm Cu. Wires | M | 0.00 | 80.00 |  | 0
117097 |  | 4C x 6.0 Sqmm Cu. Wires | M | 0.00 | 40.00 |  | 0
117098 |  | POINT WIRING - Supply, installation, testing commissioning of wiring of light points, fan points, socket outlets by using 2mm thick FRLS conduit of required dia as per IS 732, PVC conduit accessories, flexible conduit with PVC gland for drops with accessories 2R X 1.5Sqmm + 1 Sqmm FRLS Cu. Wire approved 5A modular type switches and sockets, GI or PVC boxes, and other point wiring accessories and carrying out surface or concealed conduit point wiring. All points shall be earthed with 1sqmm FRLS flexible copper wire. Points shall be terminated at light fixtures with ferrules, 15A 4 way connector; wire ends shall not be loose or bare. The rate shall include necessary civil works for embedding conduits and boxes |  | 0.00 | 0.00 |  | 0
117099 |  | 1 light point controlled by a 6A switch (Signage or LED strip) | Nos. | 0.00 | 2.00 |  | 0
117100 |  | 4 light points controlled by 6A switch (Track or Spot Lights) | Nos. | 0.00 | 1.00 |  | 0
117101 |  | 6 light points controlled by 6A switch | Nos. | 0.00 | 1.00 |  | 0
117102 |  | SWITCH AND SOCKETS AND MS ENCLOSURE UNITS - Supply, installation, testing commissioning of flush mounted plate type switch, sockets and switch + sockets of approved make or type housed in MS or GI enclosure, duly wired and painted. All the switch sockets are without boxes since the same is covered under different item |  | 0.00 | 0.00 |  | 0
117103 |  | 6A- 5pin universal socket with switch | Nos. | 0.00 | 3.00 |  | 0
117104 |  | 6A -One way plate type switch | Nos. | 0.00 | 1.00 |  | 0
117105 |  | 6 or 16- 6 pin universal socket with switch | Nos. | 0.00 | 3.00 |  | 0
117106 |  | 6 or 16- 6 pin universal socket only | Nos. | 0.00 | 5.00 |  | 0
117107 |  | 16 or 25 - One way plate type switch | Nos. | 0.00 | 6.00 |  | 0
117108 |  | 25A,TP+E Industrial PC socket with plug top controlled by 32A TP D Curve MCB to Clipsal CLIWCSWP3326 (IP44) | Nos. | 0.00 | 4.00 |  | 0
117109 |  | 3M MS or GI Coated Box | Nos. | 0.00 | 10.00 |  | 0
117110 |  | 6M MS GI Coated Box | Nos. | 0.00 | 4.00 |  | 0
117111 |  | EARTHING - Supply and laying of 8 SWG GI or Copper earthing wire in PVC conduit | M | 0.00 | 25.00 |  | 0
117112 |  | SAFETY ITEMS - Shock and First Aid charts in T or W frame | Nos. | 0.00 | 1.00 |  | 0
117113 |  | First Aid Box | Nos. | 0.00 | 1.00 |  | 0
117114 |  | 415V 150mm x 150mm enamel type danger board | Nos. | 0.00 | 1.00 |  | 0
117115 |  | Drawing display board suitable for A3 size with As built drawing laminated. | Sets | 0.00 | 1.00 |  | 0
117116 |  | Rubber gloves | Pair | 0.00 | 1.00 |  | 0
117117 |  | No Admission board | Nos. | 0.00 | 1.00 |  | 0
117118 |  | MISCELLANEOUS ITEMS - Temporary lighting during the construction of the project sockets, ELCB, MCB or fuse cut-outs, wiring, etc., complete. | Nos. | 0.00 | 5.00 |  | 0