## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
149265 |  | Prices shall be based on supply, installation, testing commissioning (SITC) at site including all taxes, duties, transportation insurance etc. |  | 0.00 | 0.00 |  | 0
149266 | 1 | VRF SYSTEMS VRF OUTDOOR UNITS Supply of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on heating cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100% load . The condensing units shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply. VRF unit shall be supplied with operating panel for operation control. ODU to have standard factory coated treatment for heat rust corrosion for Condenser coil, panels, motor, electricals heat exchanger, Power Cabling etc. The condensing units shall be of following capacities Refrigeration Capacities indicated below are actual capacity. Selection to be done considering referigerant piping length and derating at @ 40°C. Vendor has to submit highlight if capacity of the unit exceed diversity factor after derating for 40°C ambient conditions. Any alteration in capacity after bidding will not be entertain. Vendor has to provide unit to meet the refrigeration requirement. Make Daikin, Toshiba, Mitsubishi Refrigeration Capacity - 14 HP | Nos | 0.00 | 1.00 |  | 0
149267 | 2.1 | VRF INDOOR UNITS Supply,Installation,Testing and Commissioning of variable refrigerant flow modular type indoor units Corded Cordless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling as well as heating mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned below. The indoor unit shall be complete with pre filter remote as per requirement. Unit shall be quoted with T-Tube flange connection kit for for higher fresh air intake. Except Hi-wall unit, all other units shall have port for fresh air intake and inbuilt drain pump. The indoor units shall be of following capacities . HIGH STATIC DUCTABLE TYPE INDOOR UNIT with CORDED REMOTE CONTROLLER Indoor Temperature NMT 22°C 2542 CFM 6.4 TR | Nos. | 0.00 | 2.00 |  | 0
149268 | 2.2 | CEILING MOUNTED TYPE COMPACT CASSETTE UNIT with CORDLESS REMOTE CONTROLLER Indoor Temperature NMT 22°C 318 CFM 0.6 TR | Nos. | 0.00 | 1.00 |  | 0
149269 | 3 | CENTRALISED REMOTE CONTROLLER Supply of the Graphic central remote Controller (Touch Screen Type) . It must act as an advanced air conditioning management system to facilitate complete control of VRF air conditioning equipment. It should be user friendly through its touch screen, icon display and color LCD display. Integratable upto 64 remote controller groups (including AHUs TFAs) and BMS compatible with ethernet Wi-Fi communication protocol for remote monitoring. In addition to basic controls such as settings for on stop, the operation mode temperature, the air quantity and auto louver can be set. If a problem occurs, an alarm code immediately shows the details of the problem. An external input terminal is provided as standard. External signals enable the following function central operation stop, demand control, emergency stop, central operation output, central alarm output. Controller shall however be suitable for future connectivity of indoor outdoor units also. Central Remote Controller | Nos. | 0.00 | 1.00 |  | 0
149270 |  | GENERAL NOTES The cost shall be included liftting shifting of each equipment material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material equipment. |  | 0.00 | 0.00 |  | 0