## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
156327 |  | SECTION-I- WIRING POINT WIRING CONDUTING |  | 0.00 | 0.00 |  | 0
156328 | 1.1 | Supply and Installation of all materials, accessories and labour for wiring for light equipment circuit main using PVC insulated stranded copper conductor FRLS wires of 1100V grade drawn through heavy gauge rigid PVC MS conduit ( The cost of the conduit will be taken separately ) using necessary conduit accessories, PVC pull junction boxes, G.I. fish wire etc. The rate shall include the cost of providing PVC insulated stranded copper conductor earth wire in each conduit alongwith other circuit main wires. Lugs to be use at both the ends. FRLS Type only. |  | 0.00 | 0.00 |  | 0
156329 | 1.1.1 | Supply Installation of 1.5 Sq.mm copper FRLS wires | Rmt | 0.00 | 30.00 |  | 50
156330 | 1.1.2 | Supply Installation of 2.5 Sq.mm copper FRLS wires | Rmt | 0.00 | 50.00 |  | 80
156331 | 1.1.3 | Supply Installation of 4 Sq.mm copper FRLS wires | Rmt | 0.00 | 30.00 |  | 100
156332 | 1.1.4 | Supply Installation of 6 Sq.mm copper FRLS wires | Rmt | 0.00 | 30.00 |  | 150
156333 | 1.1.5 | Supply Installation of 10 Sq.mm copper FRLS wires | Rmt | 0.00 | 50.00 |  | 180
156334 | 1.1.6 | Supply Installation of 16 Sq.mm copper FRLS wires | Rmt | 0.00 | 50.00 |  | 220
156335 | 1.2 | Supplying and installing all materials, accessories and labour for conduiting the accessories for light Equipment circuit main.The conduit should be Medium gauge rigid 1.6 mm thick FRLS type PVC conduits conforming to IS-2509 of 1973 . The conduits shall be clamped by G.I. PVC saddles of minimum 20 gauge or be clamps fabricated from M.S. strips of minimum 25 mm x 3 mm. The M.S. clamps supports shall be duly painted with 2 coats of red oxide and 2 coats of black enamelled paint.The clamps supports shall be fixed to the underside of the ceiling by means of nylon rawl plugs and brass screws of 3 mm size. Anchor fasteners of suitable sizes shall be provided if necessary.The conduits shall be supported at regular intervals of 500 mm. Additional supports shall be provided on either side of bends, JB s terminations. The conduits shall be bent with bending springs to provide smooth bends. Use of ready made bends shall be kept to a minimum. The jointing of PVC conduits shall be done with couplers and PVC solvent cement. Conduits to be terminated in M.S. Boxes shall be terminated with female adaptors with bushes. All conduits assembled (PVC M.S.) without wiring shall be provided with G.I. pull wire of minimum thickness of 14SWG. And end portion of the conduit to be provided with end caps where ever necessary. The cost should include the cost of heavy gauge rigid PVC conduit with necessary conduit accessories, PVC pull junction boxes, G.I. fish wire etc laying of the same. FRLS Only |  | 0.00 | 0.00 |  | 0
156336 | 1.2.2 | 25mm PVC Conduit | Rmt | 0.00 | 100.00 |  | 120
156337 | 1.2.5 | PVC Flexible Conduit Dia 25 mm | Rmt | 0.00 | 150.00 |  | 40
156338 | 1.2.8 | 25mm MS Conduit | Rmt | 0.00 | 724.00 |  | 180
156339 | 1.2.9 | 32mm MS Conduit | Rmt | 0.00 | 30.00 |  | 210
156340 | 1.2.10 | 40mm MS Conduit | Rmt | 0.00 | 60.00 |  | 260
156341 | 1.2.12 | MS Flexible Conduit Dia 25 mm | Rmt | 0.00 | 500.00 |  | 80
156342 | 1.4 | Same Item with MS Conduit |  | 0.00 | 0.00 |  | 0
156343 | 1.4.1 | Primary light points including the cost of 5A switch (Average - Length upto 18 Mtrs) | Nos | 0.00 | 18.00 |  | 1800
156344 | 1.4.2 | Primary light points directly controlled from DB (Average - Length upto 18 Mtr) | Nos | 0.00 | 3.00 |  | 1800
156345 | 1.6 | Same Primary Point Item with MS Conduit | Nos | 0.00 | 8.00 |  | 1800
156346 | 1.6.1 | Same Secondary Point Item with MS Conduit | Nos | 0.00 | 12.00 |  | 1200
156347 | 1.8 | Same Primary Point Item with MS Conduit | Nos | 0.00 | 16.00 |  | 1800
156348 | 1.8.1 | Same Secondary Point Item with MS Conduit | Nos | 0.00 | 22.00 |  | 1200
156349 | 1.10 | Same Item with MS Conduit | Nos | 0.00 | 2.00 |  | 1200
156350 | 1.11.1 | Same Item with MS Conduit | Nos | 0.00 | 8.00 |  | 1200
156351 | 1.12 | Circuit WIRING |  | 0.00 | 0.00 |  | 0
156352 | 1.12.1 | Circuit mains wiring using 2 runs of 2.5 sq.mm +1x2.5 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 0.00 | 240.00 |  | 210
156353 | 1.12.2 | Circuit mains wiring using 2 runs of 4 sq.mm +1x4 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 0.00 | 550.00 |  | 260
156354 | 1.12.3 | Circuit mains wiring using 2 runs of 6 sq.mm +1x6 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 0.00 | 300.00 |  | 360
156355 | 1.12.4 | Circuit mains wiring using 4 runs of 4 sq.mm +2x4 Sqmm FRLS insulated copper wires in existing Conduit. | Mtr | 0.00 | 200.00 |  | 290
156356 | 1.12.5 | Circuit mains wiring using 4 runs of 6 sq.mm +2x6 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 0.00 | 420.00 |  | 450
156357 | 1.12.6 | Circuit mains wiring using 4 runs of 10 sq.mm +2x10 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 0.00 | 220.00 |  | 750
156358 | 1.12.7 | Circuit mains wiring using 4 runs of 16 sq.mm +2x16 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 0.00 | 150.00 |  | 950
156359 | 1.12.8 | Circuit mains wiring using 4 runs of 25 sq.mm +2x16 Sqmm FRLS insulated copper wires in existing Conduit | Mtr | 0.00 | 100.00 |  | 1950
156360 | 2.1 | Supply Installation of the following Industrial Plug Socket DBs |  | 0.00 | 0.00 |  | 0
156361 | 2.1.1 | 6 32A DP Metal Clad switch socket with SP MCB | Nos. | 0.00 | 22.00 |  | 3500
156362 | 2.1.3 | 40 63A DP Metal Clad switch socket with DP MCB | Nos. | 0.00 | 3.00 |  | 4000
156363 | 2.1.6 | 6 32A FP Metal Clad switch socket with FP MCB | Nos. | 0.00 | 13.00 |  | 4500
156364 | 2.1.7 | 40 63A FP Metal Clad switch socket with FP MCB | Nos. | 0.00 | 1.00 |  | 4500
156365 | 2.2 | Supply Installation of the following Sockets, Switches including the front plate Back boxes and all accessories |  | 0.00 | 0.00 |  | 0
156366 | 2.2.1 | 6A, Switch for lighting control. | No. | 0.00 | 18.00 |  | 150
156367 | 2.2.2 | 6A, 5 Pin Switch socket outlet | No. | 0.00 | 24.00 |  | 400
156368 | 2.2.3 | 1 no. 6 16A 6 Pin Switch Socket Outlets (Raw Power) | No. | 0.00 | 5.00 |  | 600
156369 | 2.2.4 | 1 no. 6 16A 6 Pin Switch Socket Outlets (UPS) Black Colour | No. | 0.00 | 5.00 |  | 600
156370 | 2.2.7 | 2 no. 6 16A 6 Pin Switch Socket Outlets (Raw Power) | No. | 0.00 | 6.00 |  | 1000
156371 | 2.2.8 | 2 no. 6 16A 6 Pin Switch Socket Outlets (UPS) Black Colour | No. | 0.00 | 9.00 |  | 1000
156372 | 2.2.7 | Bell Switch | No. | 0.00 | 2.00 |  | 200
156373 | 3.1 | Supply Installation of the CAT-6 information outlet with face plate. (For data) | Nos. | 0.00 | 6.00 |  | 500
156374 | 3.2 | Supply Installation of RJ11 telephone outlet with front plate | Nos. | 0.00 | 6.00 |  | 500
156375 | 3.3 | Supply Installation of CAT-6 Data cable in 20mm 25mm dia conduits | Mtr | 0.00 | 450.00 |  | 60
156376 | 3.5 | Supply Installation of 10pair Telephone Tag block with enclosure | No. | 0.00 | 1.00 |  | 100
156377 | 3.6 | TV boxes with 4 way connector | No. | 0.00 | 1.00 |  | 100
156378 | 3.7 | Supplying and fixing of television socket outlet in MS boxes | No. | 0.00 | 2.00 |  | 500
156379 | 3.8 | Supply Installation of RG-6 TV cable in 20mm 25mm dia conduits | Mtr | 0.00 | 60.00 |  | 60
156380 | 4.1.1 | LED Down lighters (Recessed Surfaces Mounted) on ceiling | Nos | 0.00 | 20.00 |  | 200
156381 | 4.1.3 | Surface mounted Batten Type luminaire with 1x28 36W | Nos | 0.00 | 40.00 |  | 200
156382 |  | SECTION-V PANELS, DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
156383 | 5.1 | Installation, Testing Commissioning of following Panels including placemnt on point (same floor), proper cable dressing upto satisfaction of site incharge |  | 0.00 | 0.00 |  | 0
156384 | 5.1.1 | Installation, Testing Commissioning of Main LT Panel as per SLD. | No. | 0.00 | 1.00 |  | 10000
156385 | 5.1.2 | Installation, Testing Commissioning of SUB LT Panel. | No. | 0.00 | 1.00 |  | 6000
156386 | 5.1.3 | Installation, Testing Commissioning of SERVO BY PASS Panel. | No. | 0.00 | 1.00 |  | 5000
156387 | 5.2 | Supply Installation Testing Commissioning of following Distribution boards Starters of following wall mounted (flush surface) as per drawings and specifications and as required. The distribution board shall be of sheet steel enclosure powder coated with all accessories and hardware as required complete. ( Double Door Type ).The DB shall have suitable insulated fork type indipendent neutral bus bars for each phase and earth terminal block to facilitate easy termination of wires. All wires inside the DBs shall be terminated using copper end terminations. ( Standard Prefebricated DB to be use.) (With necessary dummy plate as required, with cable gland plate at top and bottom with knockouts provided with hinged lockable covers |  | 0.00 | 0.00 |  | 0
156388 | 5.2.1 | 6 Way TPN with 1 nos 32 A FP MCB + 3 nos 25 A DP ELCB 100mA (30 mA) as incomer and 12 nos 6-32 A SP MCB as Outgoings | Nos. | 0.00 | 1.00 |  | 20000
156389 | 5.2.5 | 8 way SPN with 40 32 DP MCB + ELCB 100mA as Incomer and 8 nos 16A SP MCBs as outgoings | Nos. | 0.00 | 1.00 |  | 5500
156390 | 5.2.6 | 16 way SPN with 32 A DP MCB + ELCB 100mA as Incomer and 16 nos 10 10 32 A SP MCBs as Outgoings | Nos. | 0.00 | 1.00 |  | 55000
156391 | 5.2.11 | L T make star delta starter in SS Housing for 15KW Fan with auxilliary contactor arrangement for tripping switching On fan in case of fire | Nos. | 0.00 | 2.00 |  | 50000
156392 | 5.3 | Supply Installation Testing Commissioning of following MCB Switch Socket in Enclosures |  | 0.00 | 0.00 |  | 0
156393 | 5.3.2 | 40 63A FP MCB in Weather Proof Enclosure | Nos. | 0.00 | 2.00 |  | 3000
156394 | 5.3.7 | 6 32A DP MCB in Weather Proof Enclosure | Nos. | 0.00 | 4.00 |  | 1800
156395 | 5.3.10 | 40 63A FP ELCB 100mA in Enclosure Box | Nos. | 0.00 | 4.00 |  | 4500
156396 | 5.3.15 | 100A FP MCCB in Enclosure Box | Nos. | 0.00 | 1.00 |  | 12000
156397 |  | SECTION-VI -CABLING EARTHING |  | 0.00 | 0.00 |  | 0
156398 | 6.1 | Supply of Installation of Following cables 1.1 KV grade PVC XLPE insulated Armoured Aluminium Copper conductor cables. The cables shall be laid as per dwgs or on cable trays laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with earthing as specified and rate including cable Terminations Single Double compression type chrome plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete.(The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. The unit cost of the cable shall include clamps, fasteners etc. as required for proper installation. Earthing will be measured separately and need not be quoted under this item). All complete as required and as per final instruction as given by consultant site engineer. The cables should be properly dressed and to be tied to the cable trays using appropriate cable ties. |  | 0.00 | 0.00 |  | 0
156399 | 6.1.1 | 3.5 C X 300 Sq.mm AL. XLPE Armoured Cable- | Mtr | 0.00 | 80.00 |  | 1800
156400 | 6.1.5 | 3.5 C X 120 Sq.mm AL. XLPE Armoured Cable- | Mtr | 0.00 | 30.00 |  | 700
156401 | 6.1.7 | 3.5 C X 70 Sq.mm AL. XLPE Armoured Cable | Mtr | 0.00 | 50.00 |  | 550
156402 | 6.1.10 | 4 C X25 Sq.mm AL.XLPE Armoured Cable | Mtr | 0.00 | 80.00 |  | 250
156403 | 6.1.11 | 4 C X16 Sq.mm AL.XLPE Armoured Cable | Mtr | 0.00 | 80.00 |  | 200
156404 | 6.1.23 | 3C X 4 Sq.mm Cu Armoured Cable | Mtr | 0.00 | 90.00 |  | 800
156405 | 6.2 | Supply of Installation of Following Cable Trays of 2mm thick MS steel fabricated ladder type cable trays of the following sizes.Ladder type cable trays shall be fabricated from 50 x 50 x 5 mm M.S. angles on the sides with 25 x 6 mm M.S. strips welded at intervals of 300 mm. The trays shall be painted with 2 coats of red oxide 2 coats of synthetic enamel paint of approved colour. All trays should have coupler plates with 4 number of bolt and nuts of galvanized hardware.Trays should be supported at ecvery 1.5 mtr interval. |  | 0.00 | 0.00 |  | 0
156406 | 6.2.3 | 300mm wide Perforated Cable tray with support | Mtr | 0.00 | 45.00 |  | 550
156407 | 6.2.4 | 150mm wide Perforated type Cable tray with support | Mtr | 0.00 | 30.00 |  | 450
156408 | 6.3 | Supply of Installation of Following Earthing Material wire including necessary accessories, clamping to walls, cables etc. as required and interconnection between lengths as per specifications and as per good installation practice. The rate shall include all supports, accessories and hardware necessary for proper installation. (All GI strips should be welded on a lap joint practice and two coats of bitumin paint of should be applied on the same to avvoid corrosion in future. And all copper strips should be brazed on a lap joint parctice and should be insulated with PVC sleeve while running on cable trays wall.) And GI Al Cu SWG wires should be terminared using ring types lugs. |  | 0.00 | 0.00 |  | 0
156409 | 6.3.3 | 25 x 6 mm GI. Strip | Mtr | 0.00 | 50.00 |  | 280
156410 | 6.3.5 | 8 SWG hard drawn bare GI wire | Mtr | 0.00 | 400.00 |  | 60
156411 | 6.4 | Providing and laying 1C x 25 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr | 0.00 | 50.00 |  | 325
156412 | 6.4.1 | Providing and laying 1C x 16 sqmm insulated copper wire as earthing conductor including necessary accessories, clamping to walls, cables etc. as required and interconnection between lenghts as per specifications and as per good installation practice. | Mtr | 0.00 | 50.00 |  | 250
156413 | 6.4.5 | Chemical Earthing - Supply Installation Testing commissioning of Chemical earthing with GI electrode Pipe earth pits with 40 Dia, two meters length pipe with specially developed on Pipe in pipe Strip concept filled with highly conductive anticorrosive crystalline conductive mixture. The back fill is to be done by special compound which retains moisture enhance conductivity. The rate should be inclusive of making bore finish terminated in chamber, masonry chamber with concrete base, manhole, lockable cover with frame (300 x 300 mm) For dedicated Earth, make ASHOK or equivalent | Nos. | 0.00 | 4.00 |  | 6000
156414 | 7.1 | CONVENTIONAL TYPE |  | 0.00 | 0.00 |  | 0
156415 | 7.1.1 | Supply Installation of wiring for Smoke detector MCP Hooter control module etc. devices with 2C x 1.5 Sqmm FRLS Cu armored cable - | Mtr | 0.00 | 330.00 |  | 120
156416 | 7.1.2 | Supply Installation of Smoke Detector with base ,with required accessories for fixing , including cable termination etc. | Nos | 0.00 | 20.00 |  | 2000
156417 | 7.1.3 | Supply Installation of Heat Detector with base ,with required accessories for fixing , including cable termination etc. | Nos | 0.00 | 12.00 |  | 2000
156418 | 7.1.4 | Supply Installation of Manual Break glass Unit ,with required accessories for fixing , including cable termination etc. | Nos | 0.00 | 3.00 |  | 1200
156419 | 7.1.5 | Supply Installation of Hooter ,with required accessories for fixing , including cable termination etc. | Nos | 0.00 | 3.00 |  | 5500
156420 | 7.1.8 | Supply, Installation Testing Commissioning of 4 Zone Fire Panel with 30 min battery backup. The Panels should have Capability to integrated with Developer s Addressable FAP cost for the same should be included in this items | Nos | 0.00 | 1.00 |  | 300000
156421 |  | SECTION-VIII-MUSIC SYSTEM |  | 0.00 | 0.00 |  | 0
156422 | 8.2 | Supply Installation of 2c shielded Speaker cable inexisting Conduit (Conduit cost extra) | Rmt | 0.00 | 100.00 |  | 80
156423 | 8.4 | Installation of 6 9 15W speakers to be mounted on Column wall Ceiling | Nos. | 0.00 | 1.00 |  | 300
156424 | 8.5 | Installation, testing commissioning of amplifier 120W for music system suitable to operate on 230V AC 12V DC, with low impedance microphone input two auxiliary inputs, tone control, protection circuit complete for the speakers output 4 8 16 lines | Nos. | 0.00 | 1.00 |  | 1500
156425 | 8.6 | Installation of volume control cum ON OFF switch flush mounted on wall along with other electrical switch flush mounted on wall along with other electrical switches .The size and plate of the regulating knob should match with other switches nearby | Nos. | 0.00 | 1.00 |  | 200
156426 |  | SECTION-IX-SERVO STABILIZER INVERTOR UPS |  | 0.00 | 0.00 |  | 0
156427 | 9.3 | Installation of UPS with 20min battery back-up- make Online Systems | Nos. | 0.00 | 1.00 |  | 55000
156428 |  | SECTION-XI-CCTV SYSTEM |  | 0.00 | 0.00 |  | 0
156429 | 10.1 | Laying of Following Items |  | 0.00 | 0.00 |  | 0
156430 | 10.1.3 | CAT-6 UTP cable for IP CAMERA | Mtr | 0.00 | 300.00 |  | 60
156431 |  | SECTION-XI-MISCELLANEOUS |  | 0.00 | 0.00 |  | 0
156432 | 11.2 | Provision of ample amount of Temporary lights sockets during construction stage | LS | 0.00 | 0.00 |  | 0
156433 | 11.2.1 | Fixing of Hand Drier | Nos | 0.00 | 2.00 |  | 500
156434 | 11.2.2 | Fixing of Pest-O-Flash | Nos | 0.00 | 8.00 |  | 200
156435 | 11.2.5 | Fixing of Aircurtain | Nos | 0.00 | 2.00 |  | 500
156436 | 11.2.6 | Supply Laying of Rubber Mat, thinkness 10mm | Nos | 0.00 | 3.00 |  | 5500
156437 | 11.2.12 | Supply Fixing of Buzzer | Nos | 0.00 | 3.00 |  | 2000