## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
150295 |  | HVAC Equipments |  | 0.00 | 0.00 |  | 0
150296 |  | Air Handling Units (Indoor Type) Supply , Installation , testing and commissioning Of Double skin Ceiling Suspended Type air handling units of extruded aluminium section with 0.6 mm preplasticized or precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 38KG or m3 , DIDW Blower with TEFC motors, copper cooling coils as mentioned below , with aluminium fins, MERV-8 and MERV 13 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the AHU s installed under this tender shall have IE3 motor. All the cooling coils shall be AHRI or Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp Temperature. Approval of AHU Technical Data by consultant prior to fabrication is required. kinldy note it include fixing with proper MS support or vibration pads, electrical connections or installation and commisisoning in all aspects with CFM report to be handover with proper sign off from airport engg team. Design Parameters- 25 deg C -R.A.Temp, 55% RH, 9 deg C- CHW IN Water Flow Rate- 2.0 GPM or TR |  | 0.00 | 0.00 |  | 0
150297 |  | Ceiling Suspended Type - 3910 CMH(2500 CFM) at 15 mm External Static Pressure, 6 RD Cooling Coil, Approx 6.0 TR, 1 x 1.1 KW Motor | Nos | 0.00 | 1.00 |  | 0
150298 |  | Digital Cooling Thermostat for Air Handling Units with all accessories including gauges for checking in and out temperature etc. | Nos. | 0.00 | 1.00 |  | 0
150299 |  | Kitchen Scrubber (Dry Type) Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14 inch deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM). kinldy note it include fixing with proper MS support or vibration pads, electrical connections or installation and commisisoning in all aspects with CFM report to be handover with proper sign off from airport engg team. The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air Operating Voltage 220V, 50 Hz Ionizing Voltage 12.5 to 13 KVDC Collector Cell Voltage 6 to 6.5 KVDC Power Consumption Not more than 50W per cell. 2300 CFM | Nos | 0.00 | 2.00 |  | 0