## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
166444 | C | AC PIPING AND ACCESSORIES |  | 0.00 | 0.00 |  | 0
166445 |  | AC CONDENSATE DRAIN PIPE |  | 0.00 | 0.00 |  | 0
166446 | C.1 | Supply, installation and testing of Rigid uPVC condensate drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. |  | 0.00 | 0.00 |  | 0
166447 | C.1.1 | 20 mm Ø | Mtr | 0.00 | 7.00 |  | 0
166448 |  | AC CHILLED WATER PIPING |  | 0.00 | 0.00 |  | 0
166449 | C.2 | Supply, installation and testing of MS class (C) Chilled water pipes with insulation of approved make with vapor barrier and finished with protective coating (Pidilite Equivalent) over a layer of 7 Mil glass cloth for mechanical protection complete with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports etc. Piping insulation shall be expanded polyurethane foam with 36 kg m3 minimum density, thickness as specified below, 85% minimum closed cell content and thermal conductivity of 0.019 W m.k at 10°C. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works. |  | 0.00 | 0.00 |  | 0
166450 | C.8.1 | 25 mm Ø - (Insulation - 30 mm thick) | Nos | 0.00 | 10.00 |  | 0
166451 | D | AC PIPING VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
166452 | D.1 | Supply, installation, testing Commissioning of FCU Valve Kit of approved make for HVAC fan coil units in heating cooling systems for FCUs. Complete with pressure independent control valve with proportional linear actuator (Modulating type), three-way shut-off valves, integrated by-pass, Venturi device with pressure test ports , Shut Off valve with Strainer and pre-formed shell insulation made of PPE. Flexible connector with threaded nuts clamps to be provided between the unit and kit of suitable length. |  | 0.00 | 0.00 |  | 0
166453 | D.1.1 | 25 mm Ø | Nos | 0.00 | 1.00 |  | 0
166454 | D.2 | Supply, Installation, Testing, and Commissioning BTU Meter of approved make with direct pipe connection type or operated via sensor module connected supply and return pipe with all necessary fixing and valve arrangements. LCD display (shows all water parameters), with flow rate, temperature inputs, data storage up to 365 days. The display panel shall be mounted at readable height and it shall include interconnecting wiring between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box with all necessary fixing arrangements. Unit shall be compatible with facility Building Management System. (Make and model shall be as per Airport requirement) |  | 0.00 | 0.00 |  | 0
166455 | D.2.1 | 25 mm Ø | Nos | 0.00 | 1.00 |  | 0
166456 | D.3 | Supply, Installation, Testing, and Commissioning of Forged Brass Drain Valve Drain Cock, of approved make rubber seal, O rings e with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
166457 | D.3.1 | Drain Valve connected in chilled water supply return line | Nos | 0.00 | 1.00 |  | 0
166458 | D.4 | Supply, Installation, Testing, and Commissioning of Forged Brass Automatic Air Vent of approved make with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
166459 | D.4.1 | Automatic Air Vent connected in chilled water supply return line | Nos | 0.00 | 1.00 |  | 0
166460 | D.5 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
166461 | D.5.1 | Dial Size - 63 mm Ø | Nos | 0.00 | 1.00 |  | 0
166462 | D.6 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. |  | 0.00 | 0.00 |  | 0
166463 | D.6.1 | Dial Size - 63 mm Ø | Nos | 0.00 | 1.00 |  | 0
166464 | D.7 | Supply, installation, testing commissioning of Test point of approved make with all necessary fixing arrangements.. |  | 0.00 | 0.00 |  | 0
166465 | D.7.1 | Test point for supply and return lines | Nos | 0.00 | 1.00 |  | 0
166466 | E | AIR DISTRIBUTION DUCTS RECTANGULAR DUCTS |  | 0.00 | 0.00 |  | 0
166467 | E.1 | Supply, installation and testing of Galvanized Iron (GI) Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport local regulatory or approval body having jurisdiction. |  | 0.00 | 0.00 |  | 0
166468 | E.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 0.00 | 4.00 |  | 0
166469 |  | FLEXIBLE DUCTS |  | 0.00 | 0.00 |  | 0
166470 | E.2 | Supply, installation, and testing of Insulated Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by air handling units or any other equipment s connected to the duct with air tight fittings with all necessary accessories. |  | 0.00 | 0.00 |  | 0
166471 | E.2.1 | For FCU | Nos | 0.00 | 1.00 |  | 0
166472 | F | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS ACCOUSTIC LINNINGS |  | 0.00 | 0.00 |  | 0
166473 |  | AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS |  | 0.00 | 0.00 |  | 0
166474 | F.1 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg m3 Quote shall be inclusive of necessary Adhesive. Thermal conductivity of the insulation material shall not exceed 0.047 W m K at an average temperature of 20°C. |  | 0.00 | 0.00 |  | 0
166475 | F.1.1 | 15 mm thicknesses - (SAD) | Sq.mtr | 0.00 | 4.00 |  | 0
166476 | G | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS LOUVERS) GRILLES |  | 0.00 | 0.00 |  | 0
166477 | G.1 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange with all necessary fixing arrangements. powder coated finish with RAL Colour as required by ID Designer Architect. |  | 0.00 | 0.00 |  | 0
166478 | G.1.1 | Neck Size - 200 mm X 750 - (1 - Way) | Nos | 0.00 | 1.00 |  | 0
166479 | H | HVAC SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  | 0.00 | 0.00 |  | 0
166480 | H.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements. |  | 0.00 | 0.00 |  | 0
166481 | H.1.1 | Labelling Tagging for Services and Equipment s | Lot | 0.00 | 1.00 |  | 0
166482 | J | TESTING AND BALANCING |  | 0.00 | 0.00 |  | 0
166483 | J.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates | Lumpsum | 0.00 | 0.00 |  | 0
166484 | J.2 | Water balancing of Entire Chilled and Hot Water piping system to arrive the designed flow rates. | Lumpsum | 0.00 | 0.00 |  | 0
166485 | J.3 | Chilled water and Hot water pipe Pressure testing at 15kgf cm2 hydrostatics pressure for a minimum 24hrs hold time .Testing should be done in the presence of Airport Concerned Persons. | Lumpsum | 0.00 | 0.00 |  | 0
166486 | K | SHOP DRAWINGS APPROVALS |  | 0.00 | 0.00 |  | 0
166487 | K.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority regulatory bodies having jurisdiction, along with material submission approval with airport authorities. | Lumpsum | 0.00 | 0.00 |  | 0