## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
160861 | 3 | Electrostatic Precipitator Filter for Kitchen Exhaust Air Treatment |  | 0.00 | 0.00 |  | 0
160862 |  | - Construction Made of 16 gauge galvanized sheet, high bake epoxy powder coated or 2 mm mild steel plate oil proof of IP 54. - Operating Voltage 220V 1Ph 50Hz - Power consumption 50 watts per module unit up to 5000 cfm. - Pre Filter Washable type aluminum mesh pre-filter - Ionizer spring loaded Tungsten wires to create high voltage DC field 12-13 kV - Collector Plate High grade Aluminum collector plates which should be alternatively charged positive negative with large collecting area. Collector cell should be of permanent type and slide out facility for easy removal for cleaning. - Insulator Teaflon insulator. - Access door to filter section shall be equipped with safety limit switch. |  | 0.00 | 0.00 |  | 0
160863 | a) | Exhaust Air Qty -8520CFM (Approved make - APC-DS-5) | Nos | 0.00 | 1.00 |  | 0
160864 | 4 | Sheet Metal Ducting - Site Fabricated |  | 0.00 | 0.00 |  | 0
160865 |  | Rectangular Ducting in Galvanised Steel |  | 0.00 | 0.00 |  | 0
160866 | 4.1 | Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. |  | 0.00 | 0.00 |  | 0
160867 |  | Ducts to be fabricated at the jobsite. Site Fabrication work shall be limited to assembly, installation and suit to site pieces and collars droppers |  | 0.00 | 0.00 |  | 0
160868 |  | The quoted costs should include |  | 0.00 | 0.00 |  | 0
160869 |  | i) Ducts with reinforcement strengthening |  | 0.00 | 0.00 |  | 0
160870 |  | ii) Air tight joints |  | 0.00 | 0.00 |  | 0
160871 |  | iii) Accessories such as splitter, damper, guide vane etc. |  | 0.00 | 0.00 |  | 0
160872 |  | iv) Hangers and supports (Gripple Supporting method to be used wherever required) |  | 0.00 | 0.00 |  | 0
160873 |  | v) Painting with Black color paint for duct sides behind the grills. |  | 0.00 | 0.00 |  | 0
160874 |  | vi) The gasket used in case for all ducts shall be fire retardant type |  | 0.00 | 0.00 |  | 0
160875 |  | vii) Ducts shall be fully sealed with Silicon Sealant for leak tight installation. |  | 0.00 | 0.00 |  | 0
160876 |  | Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa |  | 0.00 | 0.00 |  | 0
160877 | a) | 0.80 mm (22 SWG) GSS ducting (751mm-1500mm) | Sqmt | 0.00 | 70.00 |  | 0
160878 | 4.2 | Insulation of Duct |  | 0.00 | 0.00 |  | 0
160879 |  | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish. (Make - Hira Technologies) |  | 0.00 | 0.00 |  | 0
160880 | a) | 13 mm thick | Sqmt | 0.00 | 35.00 |  | 0
160881 | 5 | ACCESSORIES |  | 0.00 | 0.00 |  | 0
160882 |  | Supply, fabrication, assembling, installation, adjusting testing of airdistribution accessories of assorted size as specified and as per approved shop drawings |  | 0.00 | 0.00 |  | 0
160883 | 5.1 | Volume Control Damper In Ducting |  | 0.00 | 0.00 |  | 0
160884 | a) | Supply, installation and adjusting of GSS Volume Control Damper within ducts complete as specified and with suitable links, levers. Blades should be opposed blade type. The blades should be mounted in nylon bushes operated by an interior wheel gear system. Manual quadrant control with position indicator to be provided to enable adjust volume of air as required. | Sqmt | 0.00 | 1.00 |  | 0
160885 | b) | Supplying fixing of black mat finish extruded aluminium opposed blade volume control dampers in supply air duct collars as per approved shop drawings and specifications | Nos | 0.00 | 3.00 |  | 0
160886 | 5.2 | Grilles |  | 0.00 | 0.00 |  | 0
160887 | a) | Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes. |  | 0.00 | 0.00 |  | 0
160888 |  | Approved Make - Cosmos |  | 0.00 | 0.00 |  | 0
160889 | i) | 300mmX300mm | Nos | 0.00 | 9.00 |  | 0
160890 | 5.3 | Mesh Terminal Grill |  | 0.00 | 0.00 |  | 0
160891 | a) | Supply Instalation Terminal Lovure with air flow movement for Exhuast Fresh Air duct outside mouth end. | Nos | 0.00 | 2.00 |  | 0