## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
107416 |  | DISTRIBUTION SWITCHGEAR Supply, installation, testing commissioning of Distribution Boards surface or flush mounted with Double door containing MCB or ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs or RCCB should be of 30mA or 100 or 300 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be D type and other MCBs shall be C category for lighting and raw power DB. Lighting power DB - VTPN DB 12 way VTPN DB I or C- 63A FP RCBO, 100mA -1 No. O or G -2 # 16 or 20 or 32A TP MCB O or G -30 # 10 or 16 or 20A SP MCB | Nos. | 0.00 | 1.00 |  | 35863.00
107417 |  | Supply, installation, testing commissioning of Switchgears.(Standard Product) |  | 0.00 | 0.00 |  | 0
107418 |  | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make | Nos. | 0.00 | 2.00 |  | 3368.96
107419 |  | 63 amps 4P MCB with 63A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make | Nos. | 0.00 | 1.00 |  | 3441.41
107420 |  | 32A Rey roll socket complete with 32 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 - kitchen power | Nos. | 0.00 | 4.00 |  | 2354.65
107421 |  | 16A Rey roll socket complete with 16 amps SPMCB with 3 pin metal clad socket. | Nos. | 0.00 | 15.00 |  | 2209.75
107422 |  | CABLES ACCESSORIES Supply installation of following LT XLPE FRLS cables rated for 600 or 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 10 mtrs and ten finally with metal identification tags showing the size and the location from or to the specific Panel or DB at both ends. 4C x 6 Sq. mm 2XFY Cable ( Cu ) (Kitchen 3Ph equipments | Mtr. | 0.00 | 15.00 |  | 370.95
107423 |  | Termination of following sizes of cables with Single compression cable gland.(COMET or BRAKO) 4C x 6 Sq. mm 2XFY Cable ( Cu ) (Kitchen 3Ph equipments) | Nos. | 0.00 | 2.00 |  | 297.05
107424 |  | WIRING ACCESSORIES Notes 1) Rates for point wiring shall include supply installation of Wires wiring acccessories such as angle holders or ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets fixtures shall not be included in the point wiring rates. These will be counted paid separately. 2) Unless otherwise specified, all wires in point wiring shall be 2.5 sq.mm Stranded copper conductor 1.1 KV grade, I.S.I. marked (P+N+E), Fire Retardant (FRLS) PVC insulated . Wires shall be colour coded (Red, Yellow and Blue for Phases, Black for Neutral Green for earth). 3) Looping of wires shall be in fittings and switch boxes only 4) Location of switches or sockets or DBs shown on the drawings shall be confirmed with the Architect or Consultant or Project Manager before installation. 5) All Surface and concealed Conduits shall be rigid GI conduits of size not less than 20 mm dia as per applicable IS. 6)The Contractor can take more than one circuit in the same conduit provided they are of the same phase. The size of conduit shall be decided according to the number of wires in it as per applicable IS as specified. 7) Payments for light fixtures fans will be made separately as per the items given in Light Fixtures Accessories . 8) Type location of light fixtures shown in the drawings are tentative and subject to revision as per the recommendation of Architect or Consultant. The quantities (number of points and accessories) of point wiring will be revised as actual installed on account of such revisions in the layouts. 9) Circuit wiring from DBs to the switch boards or first light point shall Be included as primary points remaining points of the same looping shall be considered as Secondary points and shall be counted in nos. 10) Circuit Wiring from DB to Kitchen Power points shall be measured in running meters |  | 0.00 | 0.00 |  | 0
107425 |  | Supply, installation, testing commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included. (Normal Light) Average length Primary point - 6 mtr Secondary point - 3 mtr |  | 0.00 | 0.00 |  | 0
107426 |  | Primary Light points controlled by MCB (3R x 1.5 sqmm wire) | Nos. | 0.00 | 4.00 |  | 1430.90
107427 |  | Secondary Light points looped in the same circuit. (3R x 1.5 sqmm wire) | Nos. | 0.00 | 9.00 |  | 978.08
107428 |  | Providing point wiring for a cluster of 3 nos., 13 amps socket outlets and 1 no. 16A switch or pop up box for Computer Points or POS using 2 x 2.5 sq. mm PVC insulated copper conductor wires and minimum 2.5 Sq. mm copper conductor PVC insulated green colour earth wire for continuous earthing from NPDB to plug point in GI Conduits as specified. (maximum 4 nos. clusters shall be connected on one circuit) switch and sockets to be mounted on front plate on partitions of furniture on hot dipped GI boxes concealed in wall 16A single pole plate switch with interconnections complete as per final approval of Architect or Consultant. (Cost of FRLS PVC Conduits or Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be FRLS type ) |  | 0.00 | 0.00 |  | 0
107429 |  | Primary Point | Nos. | 0.00 | 1.00 |  | 2318.42
107430 |  | Secondary points | Nos. | 0.00 | 1.00 |  | 1956.17
107431 |  | Providing point wiring for Raw Power points 1no. 6 or 16A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 2.5 sq. mm copper conductor wires and minimum 2.5 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect or Consultant. (Cost of GI Conduit is included and switch sockets are considered elsewhere). (Wires shall be FRLS type) Note Average primary or secondary point length to be derived by Contractor, from the drawing or site provided AND + or - 1 Mtr Measured Radially. |  | 0.00 | 0.00 |  | 0
107432 |  | Primary Point | Nos. | 0.00 | 4.00 |  | 1521.46
107433 |  | Secondary points | Nos. | 0.00 | 8.00 |  | 1014.31
107434 |  | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible FRLS wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen Power Points) |  | 0.00 | 0.00 |  | 0
107435 |  | 2R x 2.5Sqmm + 1R x 2.5Sqmm Cu. Wires | Mtr. | 0.00 | 100.00 |  | 215.18
107436 |  | 2R x 4Sqmm + 1R x 2.5Sqmm Cu. Wires | Mtr. | 0.00 | 50.00 |  | 163.01
107437 |  | Supply installation of 25 mm dia. GI conduit with pull box or junction box all accessories for Kitchen Bar Power wiring as per the requirement |  | 0.00 | 0.00 |  | 0
107438 |  | - do - but conduit pipe shall be Rigid type. | Mtr. | 0.00 | 100.00 |  | 215.18
107439 |  | - do - but flexible conduit pipe | Mtr. | 0.00 | 20.00 |  | 163.10
107440 |  | Supply and installation of Perforated Cable Tray (ASIAN)out of 14 gauge GI sheet complete with necessary fixing arrangement with Anchor Fastener and all other accessories as per the final approval of the Consultant or Architect 150 x 50 x 2mm | Mtr. | 0.00 | 20.00 |  | 298.50
107441 |  | Supply, installation, testing commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect or Consultant |  | 0.00 | 0.00 |  | 0
107442 |  | 6A 5 pin Socket outlet | Nos. | 0.00 | 2.00 |  | 489.04
107443 |  | 6 or 16A 5pin switch socket outlet | Nos. | 0.00 | 12.00 |  | 543.38
107444 |  | 3nos 6 or 13A 5pin switch socket outlet | Nos. | 0.00 | 2.00 |  | 996.20
107445 |  | Data Socket | Nos. | 0.00 | 4.00 |  | 298.50
107446 |  | Telephone Socket | Nos. | 0.00 | 1.00 |  | 224.60
107447 |  | Supply, installation of temporary lighting power arrangement for construction purpose of with industrial type switch sockets or MCB s or ELCB s lighting fittings as required to finish the work for interior contractor necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules regulations as per Airport Security Department. The material shall be taken back by the contractor. | Job | 0.00 | 1.00 |  | 14490.14
107448 |  | EARTHING - Supplying erecting bare GI conductor of 8 swg for earthing purpose | Mtr. | 0.00 | 50.00 |  | 41.25