## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
125464 |  | 3400 CFM (8.5 TR) - Supply, installation, testing commissioning of Double skin construction draw thru type AIR HANDELING UNIT. Direct Driven Backward Curved Plug Fans with VFD, with Squirrel cage IE2 induction motor, GSS frame supporting frame work, Plug type fan, vibration isolators, base frame, Motor shall be suitable for operation of Variable Frequency Drive operation with 415±10% volts, 3 phase AC supply.cost included for VFD. Coils shall have 12.5 to 15 mm dia (O.D )tubes minimum 0.35 mm thick with sine wave aluminium fins firmly bonded to copper tubes assembled in zinc coated steel frame. Face and surface areas shall be such as to ensure rated capacity from each unit and such that the air velocity across the coil shall not exceed 150 meters per minute. The coil shall be pitched in the unit casing for proper drainage. The coil shall have suitable size header with DX COIL supply return connections protruding out of AHU casing by minimum 150 mm. Each coil shall be factory-tested at 21 kg per sq. m air pressure under water. Tube shall be mechanically expanded for minimum thermal contact resistance with fins. Fin spacing shall be 8 - 12 fins per cm. Water pressure drop in coil shall not exceed 10 PSIG. (Including THERMOSTAT WITH REMOTE CONTROL cable) | Nos | 0.00 | 3.00 | EXISTING CHILLED WATER TYPE CSU AHU UNITS | 284904
125465 |  | 50 mm dia - Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 15.00 | CHILLED WATER PIPING and VALVES | 1475
125466 |  | 40 mm dia - Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 10.00 | CHILLED WATER PIPING and VALVES | 1117
125467 |  | 32 mm dia - Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 6.00 | CHILLED WATER PIPING and VALVES | 936
125468 |  | 50 mm dia - Supply, delivery, Installation testing of Valves with insulation as per specifications. Butterfly Valves with steel shaft and cast iron body (PN 10) Approved Make - Zoloto | Nos | 0.00 | 2.00 | VALVES AND FITTINGS | 3886
125469 |  | 40 mm dia - Supply, delivery, Installation testing of Valves with insulation as per specifications.Butterfly Valves with steel shaft and cast iron body (PN 10) Approved Make - Zoloto | Nos | 0.00 | 4.00 | VALVES AND FITTINGS | 3336
125470 |  | 32 mm dia - Supply, delivery, Installation testing of Valves with insulation as per specifications.Butterfly Valves with steel shaft and cast iron body (PN 10) Approved Make - Zoloto | Nos | 0.00 | 2.00 |  | 2922
125471 |  | 40 mm dia - Y Strainers with cast iron fabricated steel body (PN 10) | Nos | 0.00 | 3.00 | Y Stainers | 4214
125472 |  | 40 mm dia - Supply, installation, testing and commissioning of complete set of control valve kit comprising of Two Way Control Valve of C.I body of PN16 ratings, motorized modulating actuators with linear stroke of minimum 15 mm, AHU room,one thermowell,one power supply unit of 230Vac 24Vac.Tranparent IP55 Control box for mounting Digital controller and power supply unit.The valve size shall be suitable for pipe size coil capacity | Nos | 0.00 | 6.00 | 2 way Control valve | 20246
125473 |  | P F Auto Air Vents with ball valve - 25 mm dia. | Nos | 0.00 | 6.00 |  | 2640
125474 |  | P F Purge valve - 25 mm dia. | Nos | 0.00 | 6.00 |  | 2310
125475 |  | Pressure gauges as per specification for mounting on chilled water pipe (Range 0 - 10 kg cm2) with cock and U pipe with ball valve. | Nos | 0.00 | 6.00 | Pressure Gauges | 2723
125476 |  | Temperature gauges as per specification for mounting on pipe. (Range 0 - 50°C) with brass thermowells for mounting temperature gauges on chilled water line. | Nos | 0.00 | 6.00 | Temperature Gauges | 2145
125477 |  | 32 mm - drain pipe PVC complete with fitting, U trap, Support, receiving funnel preformed 3mm insulation. | Rmt | 0.00 | 20.00 | Drain pipe | 231
125478 |  | 0.63 mm (24 SWG) GSS ducting (601mm-750mm) - Supply, fabrication, installation and testing of GSS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for GS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Oval Ducting | Sqm | 0.00 | 45.00 | Sheet Metal Ducting - Factory Fabricated | 1657
125479 |  | 13mm thick - Supplying and fixing of following thickness under deck Nitrie Rubber ( Class O type of fire retadancy). (Make - Hira Technologies) | Sqm | 0.00 | 50.00 | Insulation of Duct | 611
125480 |  | 1.09 mm (18 MSG) MS ducting (PLENUM) - Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Rectangular Ducting | Sqm | 0.00 | 15.00 | Sheet Metal Ducting - Site Fabricated | 2452
125481 |  | Supply, installation and testing of GI construction louver dampers within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system | Sqm | 0.00 | 2.00 | VOLUME CONTROL DAMPER IN DUCTING | 8168
125482 |  | Supplying fixing of black mat finish extruded aluminum opposed blade BLACK volume control dampers in supply air duct collars as per approved shop drawings and specifications | Nos | 0.00 | 6.00 |  | 2228
125483 |  | 500 x 150mm - Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes. | Nos | 0.00 | 24.00 | GRILLES | 825
125484 |  | 150mm Width - Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. | Rmt | 0.00 | 15.00 | GRILLES | 1106