## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
107738 |  | PIPING AND VALVES |  | 0.00 | 0.00 |  | 0
107739 |  | CHILLED WATER PIPING |  | 0.00 | 0.00 |  | 0
107740 |  | Supply , Installation, Testing and Commissioning of MS heavy class (Class C ) pipes cut to requird lengths and installed with all welded joints. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers, sockets etc., and hanging arrangement and floor supports as required, rigid PUF saddles, washers and check nuts etc in accordance with the approved shop drawings and specifications. All sleeves in Fire wallorslab shall be sealed using fireproof sealant. |  | 0.00 | 0.00 |  | 0
107741 |  | For Pipe sizes of 80mm dia above complete C channel support shall be provided. For floor supports, supports shall be complete with pipes of adequate size with base plate vibration isolation pads and C channel. All pipe supports channels, fastner etc. to be selected as per support depth loading as per structural consultant recommendations. |  | 0.00 | 0.00 |  | 0
107742 |  | 80mm dia | RM | 0.00 | 80.00 |  | 0
107743 |  | 65mm dia | RM | 0.00 | 25.00 |  | 0
107744 |  | 50mm dia | RM | 0.00 | 0.00 |  | 0
107745 |  | 40mm dia | RM | 0.00 | 20.00 |  | 0
107746 |  | 32mm dia | RM | 0.00 | 0.00 |  | 0
107747 |  | CONDENSATE DRAIN PIPING |  | 0.00 | 0.00 |  | 0
107748 |  | CONDENSATE DRAIN PIPING -CPVC |  | 0.00 | 0.00 |  | 0
107749 |  | Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class O fire retardant properties in tubing form . Pipes shall be of following sizes |  | 0.00 | 0.00 |  | 0
107750 |  | 40mm dia | RM | 0.00 | 0.00 |  | 0
107751 |  | 32mm dia | RM | 0.00 | 25.00 |  | 0
107752 |  | 25mm dia | RM | 0.00 | 20.00 |  | 0
107753 |  | CHW Valve Assembly- Supplying , Installing , Testing and Commissioning of valve package included 5# Isolating Valve(Butterfly Valve), 1# Double Regulating ValveorBalancing valve, 1# Two way Motorized Modulating Valve, 1# Strainer, 2# Pressure Gauge, 2#Thermometer, 1#Drain valve, 2#Test Point Air vent as per drawing etc., complete as specified. |  | 0.00 | 0.00 |  | 0
107754 |  | 80mm Dia | Nos | 0.00 | 0.00 |  | 0
107755 |  | 65mm Dia | Nos | 0.00 | 1.00 |  | 0
107756 |  | 40mm Dia | Nos | 0.00 | 2.00 |  | 0
107757 |  | FIRE STOPPING FIRE SEALING |  | 0.00 | 0.00 |  | 0
107758 |  | Sealing and fire stopping of vertical duct or pipe risers at each floor level with foam type Sealing System after installation of duct or pipe. Foam after solidifying shall have 2 hour fire rating. | SqM | 0.00 | 0.00 |  | 0
107759 |  | BMS INTERFACE |  | 0.00 | 0.00 |  | 0
107760 |  | Necessary sockets and nipples with shut off valves for mounting sensorsortransmitters on pipe line to interface the BMS system. | Lot | 0.00 | 0.00 |  | 0
107761 |  | DUCTWORKorAIR TERMINALS |  | 0.00 | 0.00 |  | 0
107762 |  | FACTORY FABRICATED or SITE FABRICATEDDUCTING |  | 0.00 | 0.00 |  | 0
107763 |  | Supply, Installation and Testing of factory fabricated GSS (class VIII-120GSM Zinc Coaing) ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI C channelsor rolled steel wires or Gripple Wire Rope Hangers Supports complete with end fixing, GI C channels etc. as approved by clientsorconsultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supplyorexhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angleorchannel arrangement as required for ducts being installed outside or within building wherever required. |  | 0.00 | 0.00 |  | 0
107764 |  | Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI C channels Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct MS angle. All duct support to be provided with check nuts (lock nuts). |  | 0.00 | 0.00 |  | 0
107765 |  | While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs. |  | 0.00 | 0.00 |  | 0
107766 |  | Ducts shall be insulated Internallyorexternally as per approved shop drawing. |  | 0.00 | 0.00 |  | 0
107767 |  | For Air-conditioning ducts |  | 0.00 | 0.00 |  | 0
107768 |  | 1mm to 750mm -- 24G GSS with TDC Joints | SqM | 0.00 | 55.00 |  | 0
107769 |  | 750mm to 1200mm -- 22G GSS with TDC Joints | SqM | 0.00 | 15.00 |  | 0
107770 |  | 1201mm to 1800mm - 20G GSS with TDC Joints | SqM | 0.00 | 0.00 |  | 0
107771 |  | 1801mm to 2100mm - 18G GSS with TDC Joints | SqM | 0.00 | 0.00 |  | 0
107772 |  | 2101mm to 2700mm - 16G GSS with TDC Joints | SqM | 0.00 | 0.00 |  | 0
107773 |  | For Mechanical Ventilation ducts |  | 0.00 | 0.00 |  | 0
107774 |  | 1mm to 750mm -- 24G GSS with TDC Joints | SqM | 0.00 | 105.00 |  | 0
107775 |  | 750mm to 1500mm -- 22G GSS with TDC Joints | SqM | 0.00 | 35.00 |  | 0
107776 |  | 1501mm to 2100mm - 20G GSS with TDC Joints- For Scrubber Ducts | SqM | 0.00 | 0.00 |  | 0
107777 |  | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM | 0.00 | 0.00 |  | 0
107778 |  | Round Ducting |  | 0.00 | 0.00 |  | 0
107779 |  | 1mm to 750mm -- 24G GSS with TDC Joints | SqM | 0.00 | 35.00 |  | 0
107780 |  | 750mm to 1200mm -- 22G GSS with TDC Joints | SqM | 0.00 | 0.00 |  | 0
107781 |  | FLEXIBLE CANVASS CONNECTIONS |  | 0.00 | 0.00 |  | 0
107782 |  | Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling unitsorductable split unitsororinline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frameorflange on both sides of approved make. | SqM | 0.00 | 7.00 |  | 0
107783 |  | Supply,Installation ,Testing and Balancing of double louvered supply air grilles as per approved shop drawings and specifications complete with key operated aluminium volume control dampers. |  | 0.00 | 0.00 |  | 0
107784 |  | a. Powder coated extruded aluminium grilles | SqM | 0.00 | 0.00 |  | 0
107785 |  | LINEAR GRILLES |  | 0.00 | 0.00 |  | 0
107786 |  | Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. |  | 0.00 | 0.00 |  | 0
107787 |  | Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. | SqM | 0.00 | 0.00 |  | 0
107788 |  | 100 mm High grilles | Rmt | 0.00 | 0.00 |  | 0
107789 |  | 150 mm High grilles | Rmt | 0.00 | 20.00 |  | 0
107790 |  | 200 mm High grilles | Rmt | 0.00 | 0.00 |  | 0
107791 |  | SUPPLY AIR DIFFUSERS (Square or Round) |  | 0.00 | 0.00 |  | 0
107792 |  | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring typeorflat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsumorgrid ceiling. The diffusers shall be of regular type and with outer dimension of 450 x 450mm, 375mmx375mm 300mmx300mm. |  | 0.00 | 0.00 |  | 0
107793 |  | Powder coated extruded aluminium diffusers of approved colour shade. |  | 0.00 | 0.00 |  | 0
107794 |  | Neck Size 300x300 or Outder Size 600x600 | Nos | 0.00 | 0.00 |  | 0
107795 |  | Neck Size 375x375 or Outder Size 600x600 | Nos | 0.00 | 0.00 |  | 0
107796 |  | Neck Size 450x450 or Outder Size 600x600 | Nos | 0.00 | 0.00 |  | 0
107797 |  | Neck Size 600x600 or Outder Size 600x600 | Nos | 0.00 | 0.00 |  | 0
107798 |  | 375 x 375 - FA Square Grill - Double Deflection Grill | Nos | 0.00 | 10.00 |  | 0
107799 |  | 450 x 200 - FA Square Grill | Nos | 0.00 | 6.00 |  | 0
107800 |  | Supply, Installation, Testing and Balancing of Round supply air diffusers with 150mm high GSS plenum with spiggot to facilitate round flexible duct connections as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring typeorflat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsumorgrid ceiling. The diffusers shall be of regular type and with outer dimension of 600 x 600mm. |  | 0.00 | 0.00 |  | 0
107801 |  | Neck Dia 300 Outer Size 375 | Nos | 0.00 | 0.00 |  | 0
107802 |  | Neck Dia 375 Outer Size 425 | Nos | 0.00 | 5.00 |  | 0
107803 |  | Neck Dia 450 Outer Size 525 | Nos | 0.00 | 0.00 |  | 0
107804 |  | RETURN AIR DIFFUSERS |  | 0.00 | 0.00 |  | 0
107805 |  | Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring type. |  | 0.00 | 0.00 |  | 0
107806 |  | Powder coated extruded aluminium diffusers of approved colour shade. | Sq Mtr | 0.00 | 2.00 |  | 0
107807 |  | Supply, Installation,Testing and Balancing of square Fresh air double deflection grill with zero deg for spot cooling but with collar dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring orflat type. |  | 0.00 | 0.00 |  | 0
107808 |  | 375x375 Powder coated extruded aluminium diffusers of approved colour shade suitable for fixing in grid ceiling. | No | 0.00 | 8.00 |  | 0
107809 |  | Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings.- For Rectangular Duct | SqM | 0.00 | 2.00 |  | 0
107810 |  | Supply, Installation and Testing of Aluminium multi blade type louver collar dampers as per the specifications and shop drawings of approved colour shade. | SqM | 0.00 | 2.00 |  | 0
107811 |  | Supply, Installation,Testing and Commissioning of motorised fire dampers suitable for at least 90 minutes fire rating as per the specifications and approved shop drawings. Quoted price shall be inclusive of copper control wiring as required. |  | 0.00 | 0.00 |  | 0
107812 |  | Bare Fire Dampers | RO | 0.00 | 0.00 |  | 0
107813 |  | Spring return action type actuator complete with control panel and temperature sensor. Torque not less than 16NM | No | 0.00 | 0.00 |  | 0
107814 |  | Supply, Installation and Testing of fresh air grilles of powder coated or anodised extruded aluminium with GI wire mesh, inlet louvers, Box type VCD bird screen, as per the approved shop drawings and specifications.Double deflection fresh air grill with damper inside to adjust flow. |  | 0.00 | 0.00 |  | 0
107815 |  | 375x375 | Nos | 0.00 | 0.00 |  | 0
107816 |  | Supply, Installation and Testing of Bird Screens with GI wire mesh to be installed at the suction of fresh airordischarge of Exhaust air as per the specifications and shop drawings. Sample of bird screen to be got approved from consultants and Clients prior to procurement. | SqM | 0.00 | 3.00 |  | 0
107817 |  | Supply, Installation and Testing of non return dampers. NRDs to be installed in the ducts as per the specifications and shop drawings.Sample of NRDs to be got approved from consultants and Clients prior to procurement. | SqM | 0.00 | 0.00 |  | 0
107818 |  | Back Draft Damper - Supply, Installation and Testing of back draft damper on AHU mouth in GSS with periphery frame blader. To be fixed in Nut Bolt with flanges. | SqM | 0.00 | 0.00 |  | 0
107819 |  | INSULATION |  | 0.00 | 0.00 |  | 0
107820 |  | ACOUSTIC LINING OF DUCTS |  | 0.00 | 0.00 |  | 0
107821 |  | Using Open Cell Nitrile Rubber |  | 0.00 | 0.00 |  | 0
107822 |  | Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kgorm3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type. |  | 0.00 | 0.00 |  | 0
107823 |  | 9mm thick lining | SqM | 0.00 | 0.00 |  | 0
107824 |  | 13mm Thick | SqM | 0.00 | 0.00 |  | 0
107825 |  | 25 mm thick | SqM | 0.00 | 45.00 |  | 0
107826 |  | Using Fibre Glass |  | 0.00 | 0.00 |  | 0
107827 |  | Supply and Application of internal acoustic lining of supplyor return air ducting using resin bonded fibre glass insulation of density not less than 32KgorCuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated aluminium sheet of 24G etc. as required for complete installation. |  | 0.00 | 0.00 |  | 0
107828 |  | 25mm thick lining | SqM | 0.00 | 0.00 |  | 0
107829 |  | THERMAL INSULATION OF DUCTS |  | 0.00 | 0.00 |  | 0
107830 |  | Supply and Application of closed cell nitrile rubber thermal insulation for FA DuctorKEA Duct Supply ducting (Inside the store) using aluminium foil faced closed cell elastomeric insulation with class O fire retardant properties as per the specifications and drawings. Cladding shall provide protection from mechanical impact, ultra voilet radiations and Scratches etc. caldding shall not have any fibre erosion. Both insulation cladding should have built in antimicrobial protection. |  | 0.00 | 0.00 |  | 0
107831 |  | 13mm Thick | SqM | 0.00 | 190.00 |  | 0
107832 |  | CHW PIPE INSULATION |  | 0.00 | 0.00 |  | 0
107833 |  | Using Closed Cell Elastomeric Insulation |  | 0.00 | 0.00 |  | 0
107834 |  | Supply and Application of 25mmor32mm thick closed cell elastomeric insulation in tubing form orflat sections for chilled water piping as per the specifications. Quoted price shall be inclusive of adhesive as per specifications. Joints shall be sealed with adhesive forming proper bonding.Quoted price shall be inclusive of 24 G aluminium cladding for chilled water piping. (Adhesive - 1K PUR FR) |  | 0.00 | 0.00 |  | 0
107835 |  | 80mm dia (25mm thick) | RM | 0.00 | 80.00 |  | 0
107836 |  | 65mm dia (25mm thick) | RM | 0.00 | 25.00 |  | 0
107837 |  | 50mm dia (25mm thick) | RM | 0.00 | 0.00 |  | 0
107838 |  | 40mm dia (25mm thick) | RM | 0.00 | 20.00 |  | 0
107839 |  | 32mm dia (25mm thick) | RM | 0.00 | 0.00 |  | 0
107840 |  | ELECTRICAL WORKS |  | 0.00 | 0.00 |  | 0
107841 |  | CABLING |  | 0.00 | 0.00 |  | 0
107842 |  | Supply, laying, affecting connections and Testing of the following sizes of 1.1 KV armored PVC insulated aluminiumor copper conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays to be installed inside and GI trays to be installed outside exposed and 8SWG copper earth wire for AHUs.All cables shall be FRLS type. |  | 0.00 | 0.00 |  | 0
107843 |  | 3 C x 16 Sqmm cable (Copper) | RM | 0.00 | 0.00 |  | 0
107844 |  | 3 C x 10 Sqmm cable (Copper) | RM | 0.00 | 0.00 |  | 0
107845 |  | 4 C x 6 Sqmm Ar. Cable (Copper) | RM | 0.00 | 30.00 |  | 0
107846 |  | 4 C x 4 Sqmm Ar. Cable (Copper) | RM | 0.00 | 90.00 |  | 0
107847 |  | 3 C x 2.5 Sqmm cable (Copper) | RM | 0.00 | 0.00 |  | 0
107848 |  | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM | 0.00 | 0.00 |  | 0
107849 |  | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM | 0.00 | 0.00 |  | 0
107850 |  | 4 C x 1.5 Sqmm cable( Copper Control cabling) | RM | 0.00 | 0.00 |  | 0
107851 |  | Supply of Installation of Following Cable Terminations including SingleorDouble compression type chrome plated brass glands and lugs(crimping type), PVC taping as required and all accessories complete. |  | 0.00 | 0.00 |  | 0
107852 |  | 3 C x 16 Sqmm cable (Copper) | Nos | 0.00 | 0.00 |  | 0
107853 |  | 3 C x 10 Sqmm cable (Copper) | Nos | 0.00 | 0.00 |  | 0
107854 |  | 4 C x 6 Sqmm Ar. Cable (Copper) | Nos | 0.00 | 4.00 |  | 0
107855 |  | 4 C x 4 Sqmm Ar. Cable (Copper) | Nos | 0.00 | 6.00 |  | 0
107856 |  | 3 C x 2.5 Sqmm cable (Copper) | Nos | 0.00 | 0.00 |  | 0
107857 |  | 3 C x 2.5 Sqmm cable( Copper Control cabling) | Nos | 0.00 | 0.00 |  | 0
107858 |  | 3 C x 1.5 Sqmm cable(Copper Control cabling) | Nos | 0.00 | 0.00 |  | 0
107859 |  | 4 C x 1.5 Sqmm cable( Copper Control cabling) | Nos | 0.00 | 0.00 |  | 0
107860 |  | DRAIN PUMP |  | 0.00 | 0.00 |  | 0
107861 |  | Providing fixing Drain Pump in heavy efficiency for 5700 CFM AHU unit including with fitting Etc. | Nos. | 0.00 | 0.00 |  | 0
107862 |  | Lifting equipment by Staircase |  | 0.00 | 0.00 |  | 0
107863 |  | Making suitable arrangement for lifting placing of Scrubber, Air washer units from ground Floor to the mall 7th floor terrace area..Unit to be brought in dismantle condition. Assemnly to be done on site | LorS | 0.00 | 0.00 |  | 0