## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
172279 | 1 | DUCTING Supply, fabrication and erection of following gauges of G.S.S. ducting complete with elbows spliters, supports suspenders bends, tees, vanes, double canvas connection of the equipment etc., all complete as required. GI Sheet Makes Tata, Jindal, SAIL, Ispat Make Rola Star, Zeco Ductofab Note - Ducting Quantity will vary as per actual site condition. |  | 0.00 | 0.00 | Sheet Makes : Tata, Jindal, SAIL, Ispat | 0
172280 | i | 24 G | Sqmt. | 0.00 | 450.00 |  | 0
172281 | ii | 22 G | Sqmt. | 0.00 | 270.00 |  | 0
172282 | 2 | MS angle along with red oxide primer and paint along with welding, drill holes for Nut Bolt for Duct Jointing and support of ducts. Note - Quantity will vary as per actual site condition. | Kg | 0.00 | 1000.00 |  | 0
172283 | 3 | DUCTING INSULATION SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density 48 Kg CuM. Thermal conductivity, < 0.033 W m.K at 24 degC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, Class O for non-combustible grade. Makes UP Twiga, Owens Corning, Supreme Note - Actual Quantity will vary as per actual site condition. |  | 0.00 | 0.00 |  | 0
172284 | ii | 80 -mm Thick | Sqmt. | 0.00 | 600.00 |  | 0
172285 | 1 | Supply Return diffuser from TOP. Supply, installation, testing and commissioning of extruded aluminium supply and exhaust air grille with without dampers duly powder coated as per specifications and drawings. |  | 0.00 | 0.00 |  | 0
172286 | i | 600mm x 600mm | NOS. | 0.00 | 14.00 |  | 0
172287 | 2 | EXTRUDED ALUMINIUM CEILING GRILLES Supply, Installation, Testing and Balancing of Powder coated aluminium grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square rectangular Linear). The grilles shall be with 15 30 45° deflections as per requirement. The Colour shall be decided and approved by client and architect. Make Cosmos, Air Master System Air Square Rectangular Linear | Sq.mtr | 0.00 | 3.00 |  | 0
172288 | 4 | VOLUME CONTROL DAMPER G.I. Duct Volume Control Damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. With suitable ducts lever and guadrants for manual control of volume of air flow. Note - Minimum applicable charges are 0.2 sq.mtr. for any damper size. | Sqmt | 0.00 | 1.50 |  | 0
172289 |  | VCD for Exhaust Hoods | Sqmt | 0.00 | 1.00 |  | 0
172290 |  | Providing and fixing of powder coated extruded aluminium exhaust air louvers fresh air louvers with bird screen and mounting arrangement as per specification and drawings. |  | 0.00 | 0.00 |  | 0
172291 |  | Fresh Exhaust Air Louvers with VCD and Bird Screen | Sqmt | 0.00 | 1.50 |  | 0
172292 | 5 | Motorised Fire Dampers |  | 0.00 | 0.00 |  | 0
172293 |  | Supply, installation, testing commissioning of motorised fire smoke damper (spring return type) of approved make of atleast 90 min fire rating as per UL555, made out of 16 ga GSS and suitable for duct mounting with a flange of25 40 mm and depth of 150 mm. and as per the specification detail given earlier in the relevant section. The fire damper shall be complete with electrically operated actuator and modbus compatible control panel and a supervisory controller (suitable for interconnecting upto 99 controllers) complete with all interlocking control wiring. The fire dampers shall be located in the supply return ducts, at all fire rated crossovers(shafts walls etc.). The control panel shall recieve signal from affected floor fire panel and shall actuate the dampers of affected floor , one floor above and one floor below (NC to NO). All other Fire Dampers to remain NC only. The Signal to the controllers from Fire Panel to be provided by electrical agency and Controller looping interlocking and looping with supervisory controller shall be in the scope of HVAC Vendor.(Cabling price separately considered in Part C below) |  | 0.00 | 0.00 |  | 0
172294 |  | Fire Dampers | Sqm. | 0.00 | 1.00 |  | 0
172295 |  | Actuators for motorized dampers | Nos. | 0.00 | 2.00 |  | 0
172296 | 6 | CANVAS CONNECTION Supply fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass neoprene coated fibre glass. |  | 0.00 | 0.00 |  | 0
172297 | a | CHW AHU | No. | 0.00 | 1.00 |  | 0
172298 | b | Cabinet Exhaust Fan | No. | 0.00 | 1.00 |  | 0
172299 | c | Cabinet Fresh Air Fan | No. | 0.00 | 1.00 |  | 0
172300 | 7 | ELECTRICAL WORKS |  | 0.00 | 0.00 |  | 0
172301 | 7.1 | Power Cable Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor. |  | 0.00 | 0.00 |  | 0
172302 | a | CU Armoured Cable for Suitable 2400 CFM AHU Fan, 3PH Fan | Rmt | 0.00 | 5.00 |  | 0
172303 | b | CU XLPE Cable for 4500 CFM EX Fan, 3PH Fan with Industrial Top Plug | Rmt | 0.00 | 5.00 |  | 0
172304 | c | CU XLPE Cable for 3600 CFM FA Fan, 3PH Fan with Industrial Top Plug | Rmt | 0.00 | 5.00 |  | 0
172305 | c | CU XLPE Cable for dry Scrubber, 1PH with Industrial Top Plug | Rmt | 0.00 | 5.00 |  | 0
172306 | d | 8 SWG GI Earthing | Rmt | 0.00 | 10.00 |  | 0
172307 | 7.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
172308 |  | Supply Making of Cable termination of armoured unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY copper for 2XFY YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing commissioning of cables, meggaring values submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools dies shall be arranged by contractor. |  | 0.00 | 0.00 |  | 0
172309 | a | CU Armoured Cable for Suitable 2400 CFM AHU Fan, 3PH Fan | Nos. | 0.00 | 2.00 |  | 0
172310 | b | CU XLPE Cable for 4500 CFM EX Fan, 3PH Fan with Industrial Top Plug | Nos. | 0.00 | 2.00 |  | 0
172311 | c | CU XLPE Cable for 3600 CFM FA Fan, 3PH Fan with Industrial Top Plug | Nos. | 0.00 | 2.00 |  | 0
172312 | 7.3 | CABLE TRAYS |  | 0.00 | 0.00 |  | 0
172313 |  | Supplying Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall suspended from the ceiling with necessary MS supports. |  | 0.00 | 0.00 |  | 0
172314 | a | 50mm x 50mm x 1.6mm Thick | Rmt | 0.00 | 20.00 |  | 0
172315 |  | General Guidelines Ducting 1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C for air conditioning ducting. 2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg m33) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W (M·K)) at 0°C.4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil grease cleaning purpose.5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia As per duct size.8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident. 10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.11) Trap door with proper access to be provided for filter and copper coil cleaning.12) Kitchen ventilation shall comply to NFPA 96 guideline.Chilled Water Piping - 1. Chilled water piping shall be confirming to IS 1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) 1S 1239 Part-II HEAVY ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections thredolets weldolets are not allowed by puncturing the pipe. Only equal unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge temperature gauge Air vent Drain point etc.3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.6. For ceiling suspended chilled water pipe Pipe should be hanged with tie rod of size minimum 10 mm dia. 7. Attached CHW P ID drawing sketch to be followed during onsite work. |  | 0.00 | 0.00 |  | 0