## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
118889 |  | Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth |  | 0.00 | 0.00 |  | 0
118890 |  | 50 mm dia | RFt | 0.00 | 45.00 |  | 0
118891 |  | 40 mm dia | RFt | 0.00 | 45.00 |  | 0
118892 |  | VALVES AND FITTINGS |  | 0.00 | 0.00 |  | 0
118893 |  | Supply, delivery, Installation testing of Valves with insulation as per specifications. |  | 0.00 | 0.00 |  | 0
118894 |  | Approved Make - Zoloto |  | 0.00 | 0.00 |  | 0
118895 |  | Butterfly Valves with steel shaft and cast iron body (PN 10) |  | 0.00 | 0.00 |  | 0
118896 |  | 50 mm dia | Nos | 0.00 | 2.00 |  | 0
118897 |  | 40 mm dia | Nos | 0.00 | 4.00 |  | 0
118898 |  | Y Strainers with cast iron fabricated steel body (PN 10) |  | 0.00 | 0.00 |  | 0
118899 |  | 40 mm dia | Nos | 0.00 | 2.00 |  | 0
118900 |  | 2 way Control valve |  | 0.00 | 0.00 |  | 0
118901 |  | Supply, installation, testing and commissioning of complete set of control valve kit comprising of Two Way Control Valve of C.I body of PN16 ratings, motorized modulating actuators with linear stroke of minimum 15 mm, AHU room,one thermowell,one power |  | 0.00 | 0.00 |  | 0
118902 |  | 40 mm dia | Nos | 0.00 | 4.00 |  | 0
118903 |  | Auto Air Vents with ball valve - 25 mm dia. | Nos | 0.00 | 4.00 |  | 0
118904 |  | Purge valve - 25 mm dia. | Nos | 0.00 | 4.00 |  | 0
118905 |  | Pressure Gauges |  | 0.00 | 0.00 |  | 0
118906 |  | Pressure gauges as per specification for mounting on chilled water pipe (Range 0 - 10 kg cm2) with cock and U pipe with ball valve. | Nos | 0.00 | 4.00 |  | 0
118907 |  | Temperature Gauges |  | 0.00 | 0.00 |  | 0
118908 |  | Temperature gauges as per specification for mounting on pipe. (Range 0 - 50°C) with brass thermowells for mounting temperature gauges on chilled water line. | Nos | 0.00 | 4.00 |  | 0
118909 |  | Drain pipe |  | 0.00 | 0.00 |  | 0
118910 |  | drain pipe PVC complete with fitting, U trap, Support, receiving funnel preformed 3mm insulation. |  | 0.00 | 0.00 |  | 0
118911 |  | 32 mm | RFt | 0.00 | 45.00 |  | 0
118912 |  | Sheet Metal Ducting - Factory Fabricated |  | 0.00 | 0.00 |  | 0
118913 |  | OVAL Ducting in Galvanised Steel |  | 0.00 | 0.00 |  | 0
118914 |  | Supply, fabrication, installation and testing of GSS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for GS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume contro |  | 0.00 | 0.00 |  | 0
118915 |  | Ducts to be fabricated at the jobsite. factory Fabrication work shall be limited to assembly, installation and suit to site pieces and collars droppers |  | 0.00 | 0.00 |  | 0
118916 |  | The quoted costs should include |  | 0.00 | 0.00 |  | 0
118917 |  | i) Ducts with reinforcement strengthening |  | 0.00 | 0.00 |  | 0
118918 |  | ii) Air tight joints |  | 0.00 | 0.00 |  | 0
118919 |  | iii) Accessories such as splitter, damper, guide vane etc. |  | 0.00 | 0.00 |  | 0
118920 |  | iv) Hangers and supports (Gripple Supporting method to be used wherever required) |  | 0.00 | 0.00 |  | 0
118921 |  | v) Painting with Black color paint for duct sides behind the grills. |  | 0.00 | 0.00 |  | 0
118922 |  | vi) The gasket used in case for all ducts shall be fire retardant type |  | 0.00 | 0.00 |  | 0
118923 |  | vii) Ducts shall be fully sealed with Silicon Sealant for leak tight installation. |  | 0.00 | 0.00 |  | 0
118924 |  | Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa |  | 0.00 | 0.00 |  | 0
118925 |  | 0.63 mm (24 SWG) GSS ducting (601mm-750mm) | SqFtt | 0.00 | 490.00 |  | 0
118926 |  | Insulation of Duct |  | 0.00 | 0.00 |  | 0
118927 |  | Supplying and fixing of following thickness under deck Nitrie Rubber ( Class O type of fire retadancy). (Make - Hira Technologies) |  | 0.00 | 0.00 |  | 0
118928 |  | 13 mm thick | SqFtt | 0.00 | 538.00 |  | 0
118929 |  | Sheet Metal Ducting - Site Fabricated |  | 0.00 | 0.00 |  | 0
118930 |  | Rectangular Ducting in Galvanised Steel |  | 0.00 | 0.00 |  | 0
118931 |  | Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume c |  | 0.00 | 0.00 |  | 0
118932 |  | 1.09 mm (18 MSG) MS ducting (PLENUM) | SqFt | 0.00 | 215.00 |  | 0
118933 |  | VOLUME CONTROL DAMPER IN DUCTING |  | 0.00 | 0.00 |  | 0
118934 |  | Supply, installation and testing of GI construction louver dampers within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system | SqFt | 0.00 | 10.76 |  | 0
118935 |  | Supplying fixing of black mat finish extruded aluminum opposed blade BLACK volume control dampers in supply air duct collars as per approved shop drawings and specifications | Nos | 0.00 | 4.00 |  | 0
118936 |  | GRILLES |  | 0.00 | 0.00 |  | 0
118937 |  | Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes. |  | 0.00 | 0.00 |  | 0
118938 |  | 500 x 150mm | Nos. | 0.00 | 16.00 |  | 0
118939 |  | Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. |  | 0.00 | 0.00 |  | 0
118940 |  | 200mm Width | RFt | 0.00 | 130.00 |  | 0