## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
180787 |  | LT SWITCHGEAR and Distribution Boards - Supply, installation, testing and commissioning of Low voltage switchgear s, free standing, Cubical type, dead front, Frame and Doors 2mm, Internal Partations 1.6mm thick, Gland Plates 3mm Thick, powder coated (Paint Shade RAL 7032 or 7035), indoor type with vermin proof hinged lockable doors for each compartment, bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications comprising of ACB,MCCB and MCB horizontal and vertical aluminum bus bar, earth bus bar as per SLD. All meters shall be digital with LED display, whereever mentioned and shall have RS 485 Modbus RTU half duplex communication interface for provision of BMS connectivity and wired accordingly. Provide required NO or NC potential free contacts wires and terminal blocks in the cable alley for BMS operation (Optional).The swtichboards are to be tested as per IS 8623 -1977 specifications. The busbars are of high conductivity Al. alloy E91E IS 5082 specification and cable entries will be from either top or bottom depending on location. LT Switchgear shall be as per technical specification and single line diagram |  | 0.00 | 0.00 |  | 0
180788 |  | MDB - MDB shall be as per Single line diagram and technical specifications.(Indoor -IP 42) | Nos | 0.00 | 1.00 |  | 0
180789 |  | ISOLATORS |  | 0.00 | 0.00 |  | 0
180790 |  | 160A 4P MCCB in metallic enclosure -IP 42 | Nos | 0.00 | 1.00 |  | 0
180791 |  | 40A DP MCB in metallic enclosure -IP 42 | Nos | 0.00 | 2.00 |  | 0
180792 |  | STARTERS |  | 0.00 | 0.00 |  | 0
180793 |  | Supply and Installation of 1.5kW Similat to Motor KW of fan slelected by OEM of unit as per approved TDS DOL or STAR DELTA starter with contactor, MPCB, overload relay, ON-OFF push buttons, Auto or Manual, ON or OFF or Trip indicating lamps, NO or NC Contacts and potential free contacts with required accessories and provied universal sockets as shown in SLD, refere Single line diagram and technical specifications. Starter panel shall be supplied with space provisons with internal wring circuits and sight glass for VFD instlattions. Installation and wiring terminations for VFD will be electrical vendor scope. Supply of VFD in HVAC vendor scope. | Nos | 0.00 | 1.00 |  | 0
180794 |  | Supply and Installation of 2.2kW Similat to Motor KW of fan slelected by OEM of unit as per approved TDS DOL or STAR DELTA starter with contactor, MPCB, overload relay, ON-OFF push buttons, Auto or Manual, ON or OFF or Trip indicating lamps, NO or NC Contacts and potential free contacts with required accessories and provied universal sockets as shown in SLD, refere Single line diagram and technical specifications. Starter panel shall be supplied with space provisons with internal wring circuits and sight glass for VFD instlattions. Installation and wiring terminations for VFD will be electrical vendor scope. Supply of VFD in HVAC vendor scope. | Nos | 0.00 | 1.00 |  | 0
180795 |  | Supply and Installation of 3.0kW Similat to Motor KW of fan slelected by OEM of unit as per approved TDS DOL or STAR DELTA starter with contactor, MPCB, overload relay, ON-OFF push buttons, Auto or Manual, ON or OFF or Trip indicating lamps, NO or NC Contacts and potential free contacts with required accessories and provied universal sockets as shown in SLD, refere Single line diagram and technical specifications. Starter panel shall be supplied with space provisons with internal wring circuits and sight glass for VFD instlattions. Installation and wiring terminations for VFD will be electrical vendor scope. Supply of VFD in HVAC vendor scope. | Nos | 0.00 | 1.00 |  | 0
180796 |  | MCB Distribution boards |  | 0.00 | 0.00 |  | 0
180797 |  | 12 Way TPN MCB Distribution Board -PPI (KDB) MCB DB comprising the following Type of DB - 12 way TPN PPI MCB DB (Double Door) 100A 4P MCB - 1 No. as incomer 63A DP RCCB, 30mA, 2 Module - 3 Nos. as Sub incomer per phase 20A SP MCB, 10 kA - 29 Nos. as outgoings MCB are of C Curve 32A SP MCB, 10 kA - 1 Nos. as outgoings MCB are of C Curve The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc. | Nos | 0.00 | 1.00 |  | 0
180798 |  | 8 Way TPN MCB Distribution Board - PPI (LPDB) MCB DB comprising the following Type of DB - 8 way TPN PPI MCB DB (Double Door) 32A 4P MCB - 1 No. as incomer 25A DP RCCB, 30mA, 2 Module - 3 Nos. as Sub incomer per phase 10A SP MCB, 10 kA - 18 Nos. as outgoings MCB are of C Curve The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc. | Nos | 0.00 | 1.00 |  | 0
180799 |  | 12 Way SPN MCB Distribution Board MCB DB comprising the following Type of DB - 12 way SPN MCB DB (Single Door) 40A DP RCBO,30mA, 2 Module - 1 No. as incomer 6A SP MCB, 10 kA - 4 Nos. as outgoings MCB are of C Curve 10 or 16A SP MCB, 10 kA - 10 Nos. as outgoings MCB are of C Curve The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc. | Nos | 0.00 | 1.00 |  | 0
180800 |  | LOW VOLTAGE CABLES AND END TERMINATION |  | 0.00 | 0.00 |  | 0
180801 |  | Low voltage Aluminium conductor cables Supply and laying of 1100 V grade, XLPE insulated,extruded PVC Inner Sheathed and extruded FRLS-PVC Outer sheatehed , aluminium conductor, Armoured power cable as per specifications. The cable shall be laid in indoor trenches or cable trays as required. The cable shall be clamped at regular intervals to the suppoprts in trench or to cable trays or brick wall using MS clamps and fasteners. Rate shall exclude the cost of cable trays and termination in this item. NOTE Cables will not be procured based on BOQ only. True measurements will be taken by Contractor before ordering, based on Drawings or Site actual requirements ( Applicable to all respect Line items) |  | 0.00 | 0.00 |  | 0
180802 |  | 3.5CX 50Sqmm Alu.arm Cable | Rmt | 0.00 | 30.00 |  | 0
180803 |  | 4CX 10Sqmm Alu.arm Cable | Rmt | 0.00 | 15.00 |  | 0
180804 |  | Low Voltage Copper Conductor Cables Supply and laying of 1100 V grade, XLPE insulated,extruded PVC Inner Sheathed and extruded FRLS-PVC Outer sheatehed copper conductor, Armoured or Un armoured power cable as per specifications. The cable shall be laid in indoor trenches or cable trays as required. The cable shall be clamped at regular intervals to the suppoprts in trench or to cable trays or brick wall using MS clamps and fasteners. Rate shall exclude the cost of cable trays and termination in this item. Armoured Copper Cables |  | 0.00 | 0.00 |  | 0
180805 |  | 4Cx 16sqmm Cu Arm Cable | Rmt | 0.00 | 15.00 |  | 0
180806 |  | 4Cx 6sqmm Cu Arm Cable | Rmt | 0.00 | 100.00 |  | 0
180807 |  | 4Cx 4sqmm Cu Arm Cable | Rmt | 0.00 | 60.00 |  | 0
180808 |  | 3Cx 4sqmm Cu Arm. Cable | Rmt | 0.00 | 20.00 |  | 0
180809 |  | Copper Flexible Cables 3Cx6sqmm Cu Flexible Cable | Rmt | 0.00 | 20.00 |  | 0
180810 |  | LOW VOLTAGE CABLE END TERMINATION Supply and providing LV cable end termination for below listed cable with copper lugs, brass cable glands, tapping, crimping, etc. complete. Single Compression Glands Cable Size Below 150 Sqmm Double Compression Glands Cable size above 185sqmm and Single core cables 400sqmm and above |  | 0.00 | 0.00 |  | 0
180811 |  | 3.5CX 50 Sqmm Alu.arm Cable | Nos | 0.00 | 2.00 |  | 0
180812 |  | 4CX 10Sqmm Alu.arm Cable | Nos | 0.00 | 2.00 |  | 0
180813 |  | Armoured Copper Cables |  | 0.00 | 0.00 |  | 0
180814 |  | 4Cx 16sqmm Cu Arm Cable | Nos | 0.00 | 2.00 |  | 0
180815 |  | 4Cx 6sqmm Cu Arm Cable | Nos | 0.00 | 10.00 |  | 0
180816 |  | 4Cx 4sqmm Cu Arm Cable | Nos | 0.00 | 6.00 |  | 0
180817 |  | 3Cx 4sqmm Cu Arm. Cable | Nos | 0.00 | 2.00 |  | 0
180818 |  | Copper Flexible Cables 3Cx6sqmm Cu Flexible Cable | Nos | 0.00 | 8.00 |  | 0
180819 |  | SWITCHES AND SOCKETS Supply and install switches and Sockets System as required according to the specification, drawings and design. The installation rate of all the following accessories shall include for the supply of all materials such as passivated metal switchbox,junction boxes, switch plate, switches, conduit accessories, wires, tags, supports, fittings fixings and the like, to form complete elements and shall include for earthing the switchboxes The installation rate shall include for termination of all cables and wires into the devices, testing,commissioning and setting to work as required by the specifications. NOTE SWITCHES AND SOCKETS will not be procured based on BOQ only. True measurements will be taken by Contractor before ordering, based on Drawings or Site actual requirements ( Applicable to all respect Line items) Power Receptacles with Box |  | 0.00 | 0.00 |  | 0
180820 |  | Supply, installation, testing and Commissioning of 1 x 6 or 16A, Universal 5 pin round or flat socket controlled with 1 x 16A Switch with Indication lamp including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | 0.00 | 57.00 |  | 0
180821 |  | Supply, installation, testing and Commissioning of 1 x 6A, universal socket controlled with 1 x 6A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | 0.00 | 4.00 |  | 0
180822 |  | Power Receptacles without Box - Supply, Installation testing and commissioning of 3 nos. of 6 or 16 A, multi Pin Universal socket controlled by 1 no. 16 A common switch along with face plate, raceway or Table mounted and other necessary accessories to complete the installation. | Nos | 0.00 | 1.00 |  | 0
180823 |  | Industrial Sockets |  | 0.00 | 0.00 |  | 0
180824 |  | Supply, installation, testing and Commissioning of 16A, 1 phase Industrial Plug and Socket controlled with 16A DP MCB in a enclosure with all accessories. (IP65) | Nos | 0.00 | 7.00 |  | 0
180825 |  | Supply, installation, testing and Commissioning of 20A, 1 phase Industrial Plug and Socket controlled with 20A DP MCB in a enclosure with all accessories. (IP65) | Nos | 0.00 | 3.00 |  | 0
180826 |  | Supply, installation, testing and Commissioning of 32A, 3 phase Industrial Plug and Socket controlled with 32A 4P MCB in enclosure with all accessories.(IP65) | Nos | 0.00 | 4.00 |  | 0
180827 |  | Supply, installation, testing and Commissioning of 63A, 3 phase Industrial Plug and Socket controlled with 63A 4P MCB in enclosure with all accessories.(IP65) | Nos | 0.00 | 1.00 |  | 0
180828 |  | Supply and fixing of Blankplates | Nos | 0.00 | 2.00 |  | 0
180829 |  | Supply and fixing of 3 Pin Plug top suitable for 16 or 20A | Nos | 0.00 | 2.00 |  | 0
180830 |  | CIRCUIT MAINS - CIRCUIT MAIN FOR LIGHTING or POWER Supply and drawing of 1100V grade, multi strand FRLS insulated copper conductor wire. drawn into existing raceways or cable trays with necessary fixing accessories. |  | 0.00 | 0.00 |  | 0
180831 |  | 3 core 1.5 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways or conduits. Rate shall exclude the cost of Raceway or Conduit in this items. | Rmtrs | 0.00 | 40.00 |  | 0
180832 |  | 3 core 2.5 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways or conduits. Rate shall exclude the cost of Raceway or conduit in this items. | Rmtrs | 0.00 | 75.00 |  | 0
180833 |  | 3 core 4 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways or conduit. Rate shall exclude the cost of Raceway or conduit in this items. | Rmtrs | 0.00 | 150.00 |  | 0
180834 |  | 1 core 4 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways or conduits. Rate shall exclude the cost of Raceway or conduit in this items. | Rmtrs | 0.00 | 1750.00 |  | 0
180835 |  | 1 core 6 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways or conduits. Rate shall exclude the cost of Raceway or conduit in this items. | Rmtrs | 0.00 | 50.00 |  | 0
180836 |  | POINT WIRING - Point wiring of light, using 1100 volt grade, 3Rx1.5Sqmm multi strand FRLS insulated copper conductor flexible cable, drawn in existing raceways or Conduit. The rate shall include providing mounting boxes with tapped holes for lights switches, moulded front plates with brass screws earthing of all points using third core of the cable, For MCB Controlled Lights -DB to 1st light will be measured as circuit wiring.The point wiring shall be as per specification.Rate shall exclude the cost of MCB,Rceways in this item.(CONDUIT - GI) |  | 0.00 | 0.00 |  | 0
180837 |  | PRIMARY LIGHT POINT (Switch Control) - Primary light point means wiring from first switch control to the first light outlet. The switch and all necessary accessories would be part of primary point. . Not to include the incoming lighting circuit from MCB-DB to switch. But to include the sub-circuit if it is drawn from adjacent switch box. Ceiling flexible conduit shall be included at the drop of light fixture. | Nos | 0.00 | 12.00 |  | 0
180838 |  | SECONDARY LIGHT POINT (Switch Control) - Secondary light point means extention of light outlet from existing primary point. Same to be controlled by the existing switch of primary point. Ceiling flexible conduit shall be included at the drop of light fixture. | Nos | 0.00 | 46.00 |  | 0
180839 |  | CABLE TRAY or RACEWAYS |  | 0.00 | 0.00 |  | 0
180840 |  | Perforated Type - Supply and providing MS Perforated cable trays factory fabricated out of 2mm thick pre galvanized sheet steel, channel size 50 mm supporting angle frame at every 1.8 m, bottom angle fasteners, anchor grip bolts, synthetic enamelled painting, etc. The tray shall be suspended from ceiling using anchor bolt and angle iron supports or mounted from wall. The rate shall include all accessories like bends, elbows, tees, coupler plates, etc., which will be measured as linear measurement and fixing accessories.The rate shall include the cost of Supports |  | 0.00 | 0.00 |  | 0
180841 |  | 50 mm wide 50 mm height | Rmtrs | 0.00 | 5.00 |  | 0
180842 |  | 200 mm wide 50 mm height | Rmtrs | 0.00 | 15.00 |  | 0
180843 |  | 300 mm wide 50 mm height | Rmtrs | 0.00 | 7.00 |  | 0
180844 |  | POWDER COATED FRAME FOR MCB DB s |  | 0.00 | 0.00 |  | 0
180845 |  | Supply and Installation of DB Frame with wire ways shall be made out of 1.6mm thick CRCA sheet steel and powder coating colour shall match the colour of MCB DB s with hinged type door. 100mm x 100mm 1.6mm thick, wire ways or Raceway with 2mm thick screwed or press to fit cover with hinged type door for making Frame for MCB DB s. Complete required including installation accessories. | Rmtrs | 0.00 | 15.00 |  | 0
180846 |  | EARTHING - Supply and running of below listed sizes of electrolytic copper or GI earth conductor tapes or wires and laid along with cable or clamped to brick wall, etc., as required. |  | 0.00 | 0.00 |  | 0
180847 |  | 8 SWG GI wire for Earthing | Rmtrs | 0.00 | 40.00 |  | 0
180848 |  | 25x3mm GI Flat | Rmtrs | 0.00 | 25.00 |  | 0
180849 |  | 1Cx6sqmm Cu Flexible Cable Earthing (Green) | Rmtrs | 0.00 | 75.00 |  | 0
180850 |  | 1Cx4sqmm Cu Flexible Cable Earthing (Green) | Rmtrs | 0.00 | 50.00 |  | 0
180851 |  | Supply and installation of Earth pads made out of copper or GI busbars installed on 1100 V insulators including hardware and other minor civil works.associated works. - Busbar of 0.5 Mtr length made out of 45 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | Nos | 0.00 | 1.00 |  | 0
180852 |  | GI pipes (Electrical or IT or AV or CCTV or ACS) - Supply and laying of 2 mm thick rigid MS conduits in concealed or Open conduit system using conduit accessories like junction boxes, collars, bends, elbows, binding wires, etc. |  | 0.00 | 0.00 |  | 0
180853 |  | 32 mm dia conduit | Rmtrs | 0.00 | 10.00 |  | 0
180854 |  | 25 mm dia conduit | Rmtrs | 0.00 | 125.00 |  | 0
180855 |  | 20 mm dia conduit | Rmtrs | 0.00 | 80.00 |  | 0
180856 |  | MISCELLANEOUS ITEMS |  | 0.00 | 0.00 |  | 0
180857 |  | Supply and fixing of danger boards of appropriate voltage grade, size and style as required by Electrical Inspectorate. | Nos | 0.00 | 1.00 |  | 0
180858 |  | Supply of Rubber checkered mat of size 2000 x 1000 x 3mm thick, 11000 V grade. | Nos | 0.00 | 1.00 |  | 0
180859 |  | Supply of Standard First aid box complete with all accessories. | Nos | 0.00 | 1.00 |  | 0
180860 |  | Supply of Wooden framed glass fronted shock treatment chart as per IE rules fixed to wall. | Nos | 0.00 | 1.00 |  | 0
180861 |  | SITC of Hand held Fire Extinguisher - ABC Powder - 6 Kg with floor mount accessories | Nos | 0.00 | 1.00 |  | 0
180862 |  | Temporary Works - Preparation and Submission of as built drawings of total work executed (2 Sets hard and soft copy) | Nos | 0.00 | 1.00 |  | 0
180863 |  | LIGHT FIXTURES |  | 0.00 | 0.00 |  | 0
180864 |  | Supply Installation of LED 2x2 Grid Light (Type-1) | Nos | 0.00 | 21.00 |  | 0
180865 |  | Supply Installation of LED Recessed Mounted Type Light Fixtures (Type-2) | Nos | 0.00 | 20.00 |  | 0
180866 |  | Supply Installation of LED Hanging Light Fixtures (Type-3) | Nos | 0.00 | 3.00 |  | 0
180867 |  | Supply Installation of LED Track Light Fixtures (Type-4) | Nos | 0.00 | 9.00 |  | 0
180868 |  | Supply Installation of LED Decorative suspended lLight fixture (Type-5) | Nos | 0.00 | 1.00 |  | 0
180869 |  | Supply Installation of LED Decorative suspended lLight fixture (Type-5) | Nos | 0.00 | 4.00 |  | 0
180870 |  | UPS - Supply, Installation, Testing and Comissioning of 5 KVA 1 Phase input or 1 phase output UPS with 90 mins. Backup Battery Type SMF with racks and enclouser (Output Power Factor Unity ) | Nos | 0.00 | 1.00 |  | 0