## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
70391 | 1 | WATER SUPPLY PIPING |  | 0.00 | 0.00 |  | 0
70392 |  | Providing fixing CPVC piping with SDR 11 grade including cutting the pipes to correct length, jointing as per manufacturer recommendation, fixing with ms clamps, including necessary fittings like elbows ,tees,unions reducers,coupling, pipe nipples etc.complete, (Cold and RO water) |  | 0.00 | 0.00 |  | 0
70393 | 1.1 | 20 mm Dia | R.mt | 0.00 | 90.00 |  | 610
70394 | 1.2 | 25 mm Dia | R.mt | 0.00 | 15.00 |  | 650
70395 | 1.3 | 32mm Dia | R.mt | 0.00 | 25.00 |  | 850
70396 | 2 | Copper pipes and tubes shall be hand tempered conforming to requirements of EN 1057 ( formerly BS 2871) Table X , half and the fittings shall confirm the EN-1254-I ( Formerly BS 864 part-02). The fittings shall be end feed capillary fittings within wall ceiling floor including cutting chasing the wall floor, jointing, making connection to fixtures, equipment and piping with purposes made connectors, etc. including insulation of closed cell elastomeric nitrile rubber. thermal conductivity of elastometric nitrile rubber shall not exceed 0.038w m deg K. The insultaion should have fire performance and thickness of nitrile rubber should be 9mm (for hot water piping) |  | 0.00 | 0.00 |  | 0
70397 | 2.1 | 20mm Dia | R.mt | 0.00 | 30.00 |  | 2200
70398 | 2.2 | 25mm Dia | R.mt | 0.00 | 20.00 |  | 2500
70399 | 3 | Providing Fixing of forged brass lever operated Ball Valves (10Kg Sq.cm). Valve shall have with unions. |  | 0.00 | 0.00 |  | 0
70400 | 3.1 | 20mm Dia | Nos. | 0.00 | 13.00 |  | 2500
70401 | 3.2 | 25mm Dia | Nos. | 0.00 | 3.00 |  | 3000
70402 | 3.3 | 32mm Dia | Nos. | 0.00 | 1.00 |  | 4500
70403 | 4 | Providing ,fixing, testing and commissioning Water Meter as per requirement of IS 779 1994 including providing fixing matching Isolation valves ,strainer, non-return valve,complete with all necessary fittings etc screwed type(15Kgs Sq.cm). Valve shall have with union. |  | 0.00 | 0.00 |  | 0
70404 | 4.1 | 32 mm Dia incoming line | Nos. | 0.00 | 1.00 |  | 22500
70405 | 4.2 | 25 mm Dia incoming line | Nos. | 0.00 | 1.00 |  | 18500
70406 | 5 | Supply, installation,testing commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG cm2 pressure, Wall Mounted Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  | 0.00 | 0.00 |  | 0
70407 | 5.1 | 100 L Capacity- | Nos. | 0.00 | 1.00 |  | 0
70408 | 5.2 | 25 L Capacity- | Nos. | 0.00 | 1.00 |  | 20000
70409 | 6 | SITC of Eco smart RO-100 with all required accessories and inbuild storage | Nos | 0.00 | 1.00 |  | 0
70410 | 7 | SITC of Eco smart RO-50 with all required accessories and inbuild storage | Nos | 0.00 | 2.00 |  | 0
70411 | 8 | RO PACKAGE PLANT-Supply , installations, testing and comminissioning of Package RO plant 200 Lit Hr including required pressure pumps panel pressurised tank if any , all assesories, valves and membrance cleaning system, ultra-violet sterilizer, internal piping, presure gages etc (System shall be Auto fill stop and Auto empty start mechanisam) | Nos. | 0.00 | 0.00 |  | 0
70412 | 9 | Supply, Installation, Commissioning Testing for Booster pump for Ro water supply WITH FLOW SWITCH GRAVITATIONAL FLOW (top to bottom flow) with both side Sensor operations- A) 3CUM PER HR. B) HEAD 25M, C) PHASE SINGLE PHASE, D) PROTECTION IP55, E) MONOBLOCK TYPE, with sensors cabling Control panel.(Pump shall be Auto fill stop and Auto empty start mechanisam) |  | 0.00 | 0.00 |  | 0
70413 | 9.1 | 1 HP | Nos. | 0.00 | 0.00 |  | 18500
70414 | 9.2 | 1.5 HP | Nos. | 0.00 | 0.00 |  | 22000
70415 | 10 | Supply, Installation of sintex loft mounted water tank of 500 Ltrs | Nos. | 0.00 | 0.00 |  | 12000
70416 | 11 | P F water level Indicator on loft water tank by means of a transparent clear tube fixed along height of the water tank hence making water level visible | Nos. | 0.00 | 0.00 |  | 5000
70417 |  | TOTAL OF WATER SUPPLY |  | 0.00 | 0.00 |  | 0
70418 |  | DRAINAGE |  | 0.00 | 0.00 |  | 0
70419 | 1 | UPVC-SWR pipes (working pressure 10kg cm2) conforming to IS 13592 92 and IS 14735-type-B solvent posted ( for Dia above 50mm) and for ( Dia below 50mm) shall be as per IS 4985 and 7834 Class-05 (10 kg cm2) including cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts supported on wall hung below slab etc. with all material labor complete and as directed. [The Rate shall include supply and fixing of nesessary items] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] |  | 0.00 | 0.00 |  | 0
70420 | 1.1 | 32mm Dia | R.mt | 0.00 | 0.00 |  | 1350
70421 | 1.2 | 40mm Dia | R.mt | 0.00 | 5.00 |  | 1520
70422 | 1.3 | 50mm Dia | R.mt | 0.00 | 10.00 |  | 1652
70423 | 1.4 | 65mm Dia | R.mt | 0.00 | 35.00 |  | 1800
70424 | 1.5 | 75mm Dia | R.mt | 0.00 | 30.00 |  | 1900
70425 | 1.6 | 100 mm Dia | R.mt | 0.00 | 70.00 |  | 2200
70426 | 2 | Supply, Install PVC multi floor Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for taking 40mm Dia 50mm Dia Back Inlet Connection with 75mm Dia outlet | Nos. | 0.00 | 20.00 |  | 2250
70427 | 3 | Supply, Install PVC floor Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0.00 | 8.00 |  | 2250
70428 | 4 | Supply, Install PVC clean out plugs including fixing with necessary consumables |  | 0.00 | 0.00 |  | 0
70429 | 4.1 | 50mm Dia | Nos. | 0.00 | 0.00 |  | 0
70430 | 4.2 | 40mm Dia | Nos. | 0.00 | 0.00 |  | 0
70431 | 5 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 70 ( 104 lit) | Nos. | 0.00 | 0.00 |  | 0
70432 | 6 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 50 ( 72 lit) | Nos. | 0.00 | 2.00 |  | 75000
70433 | 7 | Supply, Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 20 ( 34.3 lit) | Nos. | 0.00 | 5.00 |  | 45000
70434 |  | TOTAL OF DRAINAGE |  | 0.00 | 0.00 |  | 0
70435 | 7 | S .S Grating - Only Installation |  | 0.00 | 0.00 |  | 0
70436 |  | Only installation of S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. (100 mm Dia S.S 304 grade finish unions reducers coupling or 75mm Dia S.S 304 grade finish unions reducers coupling or 50mm Dia S.S 304 grade finish unions reducers coupling) | Nos. | 0.00 | 8.00 |  | 35000
70437 |  | Only installation of S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS closed tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. (100 mm Dia S.S 304 grade finish unions reducers coupling or 75mm Dia S.S 304 grade finish unions reducers coupling or 50mm Dia S.S 304 grade finish unions reducers coupling) | Nos. | 0.00 | 4.00 |  | 48000
70438 |  | Only installation of S.S Grating size, 1200mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. ( at hook up point) | Nos. | 0.00 | 1.00 |  | 80000
70439 |  | Only installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. (100 mm Dia S.S 304 grade finish unions reducers coupling or 75mm Dia S.S 304 grade finish unions reducers coupling or 50mm Dia S.S 304 grade finish unions reducers coupling) | Nos. | 0.00 | 2.00 |  | 55000
70440 |  | Only installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing Site Engineer s instruction. (100 mm Dia S.S 304 grade finish unions reducers coupling or 75mm Dia S.S 304 grade finish unions reducers coupling or 50mm Dia S.S 304 grade finish unions reducers coupling) | Nos. | 0.00 | 2.00 |  | 55000
70441 |  | TOTAL OF DRAINAGE |  | 0.00 | 0.00 |  | 0
70442 |  | SANITARY AND C. P. FITTINGS FIXTURES |  | 0.00 | 0.00 |  | 0
70443 |  | Only installation, testing and commissioning of sanitary and C.P. fittings (Model no. to be specified by Arch) |  | 0.00 | 0.00 |  | 0
70444 | 1.1 | EWC with seat cover | Nos | 0.00 | 0.00 |  | 0
70445 | 1.2 | Concealed flush tank | Nos | 0.00 | 0.00 |  | 0
70446 | 1.3 | Concealed flush valve | Nos | 0.00 | 0.00 |  | 0
70447 | 1.4 | Health Faucet | Nos | 0.00 | 0.00 |  | 0
70448 | 1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0.00 | 0.00 |  | 0
70449 | 1.6 | Bided | Nos | 0.00 | 0.00 |  | 0
70450 | 1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0.00 | 0.00 |  | 0
70451 | 1.8 | Wash Basin Cock | Nos | 0.00 | 0.00 |  | 0
70452 | 1.9 | shower and mixer | Nos | 0.00 | 0.00 |  | 0
70453 | 1.1 | Jet Spray | Nos | 0.00 | 0.00 |  | 0
70454 | 1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0.00 | 0.00 |  | 0
70455 | 1.12 | Under Counter Sink including waste Coupling | Nos | 0.00 | 10.00 |  | 8500
70456 | 1.13 | Sink Pillar Cock | Nos | 0.00 | 10.00 |  | 3500
70457 | 1.14 | Bottle Trap for WHB sink and urinal with all connecting pipes | Nos | 0.00 | 10.00 |  | 2500
70458 | 1.15 | Angle Cock with PVC pipe connection upto WHB sink Geyser connection | Nos | 0.00 | 32.00 |  | 1800
70459 | 1.16 | Urinal | Nos | 0.00 | 0.00 |  | 0
70460 | 1.17 | Auto Flush Valve Sensor with connecting piping spreader for urinal(DC) | Nos | 0.00 | 0.00 |  | 0
70461 |  | SUB TOTAL -C-SANITARY AND C. P. FITTINGS FIXTURES ( ONLY INSTALLATIONS) |  | 0.00 | 0.00 |  | 0
70462 |  | NOTES |  | 0.00 | 0.00 |  | 0
70463 |  | 1) Taxes and duties shall be Extra as actual |  | 0.00 | 0.00 |  | 0
70464 |  | 2) Contractor to read the drawings with BOQ and quote accordigly, Deviation if any shall be confirmed by contcator prior to finalise the order. |  | 0.00 | 0.00 |  | 0