## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
71434 |  | Outgoings |  | 0.00 | 0.00 |  | 0
71420 |  | Busbar 100A TPN Cu Busbar |  | 0.00 | 0.00 |  | 0
71443 | 2.1 | SWITCHGEARS |  | 0.00 | 0.00 |  | 0
71461 |  | Incomer 32 AMPS DP RCBO 100mA |  | 0.00 | 0.00 |  | 0
71465 | 2.1 | POWER CABLING |  | 0.00 | 0.00 |  | 0
71431 |  | Meter Protection ELR with CBCT; 40 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  | 0.00 | 0.00 |  | 0
71437 |  | c) 32A DP MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
71449 |  | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 15.00 |  | 950
71451 | 2.2 | DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
71439 | 2 | SWITCHGEARS DISTRIBUTION BOARD |  | 0.00 | 0.00 |  | 0
71453 |  | Incomer 20 AMPS DP MCB 10KA 1 Nos. |  | 0.00 | 0.00 |  | 0
71430 |  | Incomer 40 AMPS 4P MCCB, 25kA with TM Based O C SC Release. |  | 0.00 | 0.00 |  | 0
71419 |  | Indication Phase indicating lamps with 6A MCB |  | 0.00 | 0.00 |  | 0
71454 |  | Outgoings 6 10 16 A SP MCB B Type - 4 Nos. |  | 0.00 | 0.00 |  | 0
71406 | 1.1 | MAIN PANEL-1 | Nos. | 0.00 | 0.00 |  | 0
71456 |  | Incomer 80A, FP, MCB, 10kA 1 Nos |  | 0.00 | 0.00 |  | 0
71428 |  | f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON OFF TRIP Indication, ON OFF Push Button-1 Nos. |  | 0.00 | 0.00 |  | 0
71418 |  | Meter Protection ELR with CBCT; 60 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  | 0.00 | 0.00 |  | 0
71433 |  | Busbar 75A TPN Cu Busbar |  | 0.00 | 0.00 |  | 0
71460 |  | 12 WAY SPN DB - UPS DB | Nos. | 0.00 | 0.00 |  | 0
71441 |  | Provide insulated dedicated earth link for UPS DB |  | 0.00 | 0.00 |  | 0
71422 |  | Outgoings |  | 0.00 | 0.00 |  | 0
71426 |  | a) 63A 4P MCCB, 16kA, TM BASED-1 Nos. |  | 0.00 | 0.00 |  | 0
71457 |  | Sub Incomer 63A, DP, RCCB, 100mA 3 Nos |  | 0.00 | 0.00 |  | 0
71427 |  | d) 40A DP MCB-2 Nos. |  | 0.00 | 0.00 |  | 0
71467 |  | Aluminium cables |  | 0.00 | 0.00 |  | 0
71429 | 1.2 | MAIN PANEL-2 | Nos. | 0.00 | 0.00 |  | 0
71432 |  | Indication Phase indicating lamps with 6A MCB |  | 0.00 | 0.00 |  | 0
71438 |  | d) 40A DP MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
71436 |  | b) 25A 4P MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
71452 |  | 6 WAY SPN DB - UPS DB | Nos. | 0.00 | 1.00 |  | 8500
71470 |  | 4C x 25 Sq.mm. | Mtr. | 0.00 | 25.00 |  | 465
71463 |  | TOTAL FOR DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
71471 |  | - do - but for copper cables |  | 0.00 | 0.00 |  | 0
71464 | 2 | MV CABLES |  | 0.00 | 0.00 |  | 0
71472 |  | 4C x 25 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71442 |  | All MCB s for UPS shall be D Curve, C Curve for Power B Curve for Lighting. |  | 0.00 | 0.00 |  | 0
71444 |  | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears. |  | 0.00 | 0.00 |  | 0
71455 |  | FABRICATED - LPDB | Nos. | 0.00 | 1.00 |  | 38000
71458 |  | Outgoings 10 16 20 25 A SP MCB C Type - 36 Nos. |  | 0.00 | 0.00 |  | 0
71446 |  | 63 40 32 20 amps DP MCB C TYPE with complete with all mounting accessories – IP-65 |  | 0.00 | 0.00 |  | 0
71466 |  | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp |  | 0.00 | 0.00 |  | 0
71459 |  | Outgoings 32 A SP MCB C Type - 1 Nos. |  | 0.00 | 0.00 |  | 0
71469 |  | 3.5C x 35 Sq.mm. | Mtr. | 0.00 | 5.00 |  | 420
71462 |  | Outgoings 10 16 20 A SP MCB C Type - 6 Nos. |  | 0.00 | 0.00 |  | 0
71473 |  | 4C x 16 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71474 |  | 4C x 10 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71404 | 1 | PANELS, SWITCHGEARS DISTRIBUTION BOARD |  | 0.00 | 0.00 |  | 0
71407 |  | Incomer 63 AMPS 4P MCCB, 25kA with TM Based O C SC Release. |  | 0.00 | 0.00 |  | 0
71435 |  | a) 32A 4P MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
71440 |  | Supplying installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards Switchgears. (IP-43) ACRY DB |  | 0.00 | 0.00 |  | 0
71445 |  | 63 40 32 20 amps 4P MCB C TYPE with complete with all mounting accessories – for Indoor Legrand make | Nos. | 0.00 | 1.00 |  | 1500
71447 |  | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 2.00 |  | 950
71448 |  | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 0.00 |  | 0
71450 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 10.00 |  | 350
71468 |  | 4C x 50 Sq.mm. | Mtr. | 0.00 | 10.00 |  | 560
71475 |  | 4C x 6 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71476 |  | 4C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71478 |  | 3C x 6 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71479 |  | 3C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71477 |  | 4C x 2.5 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71480 |  | 3C x 2.5 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71481 |  | CU Flexible Cables |  | 0.00 | 0.00 |  | 0
71482 |  | 4C x 6 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71483 |  | 4C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71485 |  | 3C x 2.5 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71484 |  | 3C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 |  | 0
71486 |  | 2C x 2.5 Sq.mm. for Earthing | Mtr. | 0.00 | 0.00 |  | 0
71487 |  | , - do - but for copper flexible cables |  | 0.00 | 0.00 |  | 0
71489 |  | TOTAL FOR POWER CABLES |  | 0.00 | 0.00 |  | 0
71491 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
71490 | 2.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
71492 |  | 4C x 50 Sq.mm. AL | Nos. | 0.00 | 1.00 |  | 950
71488 |  | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | Mtr. | 0.00 | 0.00 |  | 0
71494 |  | 4C x 25 Sq.mm. | Nos. | 0.00 | 1.00 |  | 850
71493 |  | 3.5C x 35 Sq.mm. | Nos. | 0.00 | 1.00 |  | 950
71495 |  | 4C x 16 Sq.mm. CU | Nos. | 0.00 | 0.00 |  | 0
71496 |  | 4C x 10 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71498 |  | 4C x 4 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71497 |  | 4C x 6 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71499 |  | 4C x 2.5 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71501 |  | 3C x 4 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71505 |  | 4C x 4 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71503 |  | Flexible cable |  | 0.00 | 0.00 |  | 0
71500 |  | 3C x 6 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71502 |  | 3C x 2.5 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71504 |  | 4C x 6 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71509 |  | TOTAL FOR POWER CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
71506 |  | 3C x 4 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71507 |  | 3C x 2.5 Sq.mm. (Lighting) | Nos. | 0.00 | 0.00 |  | 0
71510 | 3 | RACEWAYS AND CABLE TRAYS |  | 0.00 | 0.00 |  | 0
71508 |  | 2C x 2.5 Sq.mm. | Nos. | 0.00 | 0.00 |  | 0
71512 |  | 100 mm (wide) x 50 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
71511 | 3.1 | TRUNKING Fabricating supplying to site of installation, installation on ceiling surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and |  | 0.00 | 0.00 |  | 0
71513 |  | 50 mm (wide) x 50 mm (height) | Mtr. | 0.00 | 10.00 |  | 450
71514 | 3.2 | RACEWAY Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 m |  | 0.00 | 0.00 |  | 0
71516 |  | 65 mm (wide) x 40 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
71517 | 3.3 | JUNCTION BOXES Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated fla |  | 0.00 | 0.00 |  | 0
71519 |  | 250 mm x 250 x 60 50 mm (height) | Mtr. | 0.00 | 5.00 |  | 1250
71515 |  | 100 mm (wide) x 40 mm (height) | Mtr. | 0.00 | 10.00 |  | 600
71518 |  | (variation in height may be considered for quoting as floor thickness may vary) |  | 0.00 | 0.00 |  | 0
71520 |  | 150 mm x 150 x 60 50 mm (height) | Mtr. | 0.00 | 5.00 |  | 600
71521 |  | 100 mm x 150 x 60 50 mm (height) | Mtr. | 0.00 | 5.00 |  | 450
71522 | 3.4 | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she |  | 0.00 | 0.00 |  | 0
71523 |  | 300 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 0.00 |  | 0
71524 |  | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 0.00 |  | 0
71525 |  | 100 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 20.00 |  | 450
71526 |  | 50 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 10.00 |  | 360
71528 | 4 | POINT WIRING |  | 0.00 | 0.00 |  | 0
71530 |  | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. |  | 0.00 | 0.00 |  | 0
71529 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. |  | 0.00 | 0.00 |  | 0
71537 | 4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes a |  | 0.00 | 0.00 |  | 0
71531 |  | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. |  | 0.00 | 0.00 |  | 0
71534 | 4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 |  | 0.00 | 0.00 |  | 0
71533 |  | The Length shall be paid as per the actual measurements as per following manner. |  | 0.00 | 0.00 |  | 0
71538 |  | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 0.00 | 8.00 |  | 1200
71535 |  | From DB to Normal Switch Board | Mtr. | 0.00 | 200.00 |  | 205
71539 |  | First point controlled by one no. 6 amp switch. (upto 20Mtr.) | Nos. | 0.00 | 4.00 |  | 2200
71527 |  | TOTAL FOR RACEWAYS AND CABLE TRAYS |  | 0.00 | 0.00 |  | 0
71532 |  | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  | 0.00 | 0.00 |  | 0
71536 |  | From DB to Emergency Switch Board | Mtr. | 0.00 | 100.00 |  | 205
71540 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 0.00 | 8.00 |  | 1200
71542 | 4.3 | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.00 | 0.00 |  | 0
71541 |  | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) | Nos. | 0.00 | 3.00 |  | 2200
71544 | 4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed GI conduits as called for and earthing. |  | 0.00 | 0.00 |  | 0
71545 |  | First point controlled by existing MCB in D.B. | Mtr. | 0.00 | 0.00 |  | 0
71546 |  | First Emergency point controlled by existing MCB in D.B. | Mtr. | 0.00 | 0.00 |  | 0
71550 | 4.9 | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 0.00 | 0.00 |  | 0
71551 | 4.1 | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng |  | 0.00 | 0.00 |  | 0
71547 | 4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed GI conduit and earthing | Nos. | 0.00 | 0.00 |  | 0
71548 | 4.7 | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed M.S. conduit and earthing For Emergency Lighting | Nos. | 0.00 | 0.00 |  | 0
71557 | 4.12 | Supply Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV | Mtr. | 0.00 | 70.00 |  | 105
71552 |  | 20 mm dia GI Conduit | Mtr. | 0.00 | 0.00 |  | 0
71559 | 5 | MODULAR SWITCHES |  | 0.00 | 0.00 |  | 0
71561 |  | 6A One Way Switch | Nos. | 0.00 | 5.00 |  | 175
71553 |  | 25 mm dia GI Conduit | Mtr. | 0.00 | 200.00 |  | 75
71563 |  | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) | Nos. | 0.00 | 20.00 |  | 450
71558 |  | TOTAL FOR POINT WIRING |  | 0.00 | 0.00 |  | 0
71564 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 10.00 |  | 1200
71566 |  | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 0.00 | 1.00 |  | 2100
71569 |  | Telephone Outlet (RJ-11) | Nos. | 0.00 | 0.00 |  | 0
71567 |  | 20 Amp 1- Ph Electrical Outlet | Nos. | 0.00 | 0.00 |  | 0
71570 |  | TOTAL FOR MODULAR SWITCHES |  | 0.00 | 0.00 |  | 0
71573 |  | 25 x 3 mm | Mtr. | 0.00 | 0.00 |  | 0
71549 | 4.8 | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 0.00 | 50.00 |  | 350
71572 | 6.1 | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner. |  | 0.00 | 0.00 |  | 0
71560 | 5.1 | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n |  | 0.00 | 0.00 |  | 0
71562 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | Nos. | 0.00 | 1.00 |  | 350
71565 |  | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 0.00 | 0.00 |  | 0
71574 | 6.2 | Supplying and erecting bare Copper conductor of following sizes |  | 0.00 | 0.00 |  | 0
71579 |  | ROUND CEILING LIGHT 10w-20w - 3000kelvin | Nos. | 0.00 | 10.00 |  | 200
71580 |  | 600x600 square LED panel lights 36w - 6000kelvin | Nos. | 0.00 | 12.00 |  | 250
71584 |  | T5 LED WALL LIGHT 28w- 6000kevin | Nos. | 0.00 | 4.00 |  | 200
71585 | 8 | MISCELLANEOUS WORKS |  | 0.00 | 0.00 |  | 0
71587 | 8.2 | Supply fixing in position the best quality danger notice boards of approved shape size as reqd. by the local Electrical Inspecting Authority written in English, Hindi local language. | Nos. | 0.00 | 0.00 |  | 0
71603 | 9.3 | Supply, Installation, testing commissioning of addressable type Heat Detector (fixed cum-rate of rise type) with fix temperature at 78 o C complete with all fixing accessories like base, base box, etc to be installed under above false ceiling, roof and | No. | 0.00 | 2.00 |  | 1150
71604 | 9.4 | Supply, installation, testing commissioning of conventional Manual Call Point (break glass type)complete with push button,enclosed in box with provision of conduit cable coupling.The unit to be painted fire red outside ,white inside and written in case | No. | 0.00 | 1.00 |  | 140
71606 | 9.6 | Supply, installation, testing commissioning of Conventional Hooter cum Strobe complete as required.110 cd light 85 dB adjustable at different locations complete with all fixing accessories etc under false ceiling ,roof,wall etc complete as required. | No. | 0.00 | 1.00 |  | 485
71575 |  | 8 SWG | RMtr. | 0.00 | 50.00 |  | 130
71576 |  | TOTAL FOR GENERAL EARTHING |  | 0.00 | 0.00 |  | 0
71578 | 7.1 | Receiving from Store, Installation, testing commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook Rods as per final approval from Architect Client Consultant |  | 0.00 | 0.00 |  | 0
71581 |  | HANGING LIGHT | Nos. | 0.00 | 0.00 |  | 0
71598 | 8.3 | Supply, laying, testing of RG 6 Cable for CCTV. | Mrt | 0.00 | 250.00 |  | 45
71599 | 8.4 | Supply, laying, testing (for continuity) of 23 AWG Copper, Cat 6 UTP Cable, Data Wi-Fi points including end termination, dressing, bunching of cables with identification ferruling. | Mrt | 0.00 | 200.00 |  | 65
71602 | 9.2 | Supply, Installation, testing commissioning of addressable type smoke Detector with floating sensitivity Complete with all accessories like base, base box, etc. to be installed under above false ceiling, roof and concealed space, etc. complete as req | No. | 0.00 | 0.00 |  | 0
71605 | 9.5 | Supply, Installation, testing commissioning of addressable type manual call point (break glass type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and writt | No. | 0.00 | 0.00 |  | 0
71607 | 9.7 | Supply, Installation, testing commissioning of hoooters (Specification - 110 cd light 85 dB with adjustable DB) at different locations complete with all fixing accessories, etc under false ceiling roof, wall etc. complete as required. | No. | 0.00 | 0.00 |  | 0
71597 | 8.2 | Supply, installation, testing commissioning of 16 Channel Licence Server hardware based Digital Video Recorder (DVR) with 3 Client licence, Embedded OS per-loaded video recording software, Minimum 256 Mbps incoming bandwidth and 256 Mbps outgoing ba | Nos | 0.00 | 0.00 |  | 0
71609 | 9.9 | Supplying, erecting, testing and commissioning the addressable type Fire Alarm Control Panel (FACP) with standard accessories complete | Set | 0.00 | 0.00 |  | 0
71571 | 6 | GENERAL EARTHING |  | 0.00 | 0.00 |  | 0
71555 |  | 20 mm dia GI Conduit | Mtr. | 0.00 | 0.00 |  | 0
71577 | 7 | LIGHT FIXTURES INSTALLATION |  | 0.00 | 0.00 |  | 0
71582 |  | TRACK LIGHT | Nos. | 0.00 | 0.00 |  | 0
71583 |  | LED STRIP (15 M) | Mtr. | 0.00 | 0.00 |  | 0
71586 | 8.1 | Supply fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame covered with clear glass. | Nos. | 0.00 | 0.00 |  | 0
71610 | 9.1 | Supplying and erecting PVC armoured cable 2 core 1.5 sq. mm FRLS copper conductor complete erected on wall celling as per specification | Mtr. | 0.00 | 50.00 |  | 115
71590 | 8 | CCTV System |  | 0.00 | 0.00 |  | 0
71601 | 9.1 | Supply, installation, testing commissioning of Conventional Type optical Smoke Detector with inbuilt scattered light measurement, rate of rise and fixed temperature based technology and LED indication should be on the centre of the detector with mountin | No. | 0.00 | 6.00 |  | 1150
71611 | 9.11 | Supply installation testing and comissioning of Hood supression system(Ceasefire or equivalent). | No. | 0.00 | 0.00 |  | 0
71543 | 4.4 | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed GI conduit and earthing For Emergency Light | Nos. | 0.00 | 0.00 |  | 0
71554 | 4.11 | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the l |  | 0.00 | 0.00 |  | 0
71556 |  | 25 mm dia GI Conduit | Mtr. | 0.00 | 50.00 |  | 50
71568 |  | Data Outlet (RJ-45) | Nos. | 0.00 | 0.00 |  | 0
71588 | 8.3 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical ELV Services executed at site. | Part of Tender | 0.00 | 0.00 |  | 0
71592 | 8.1 | Supply Installation, testing commissining of Indoor type Analogue Dome Camera with 1 2 2 Mega Pixel, integrated 4 6mm Fixed lens, Full HD high definition, Inbuilt Smart IR LED upto 10m distance, 0.02 lux color 0 lux with IR LEDs on, H.264, H.265 high | Nos. | 0.00 | 0.00 |  | 0
71600 | 9 | Fire Detection and Alarm System | LOT | 0.00 | 0.00 |  | 1150
71608 | 9.8 | Supply, installation, testing commissioning of 2 zone based conventional Fire alarm control panel with standard set complete as required. | Set | 0.00 | 1.00 |  | 13000