## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
149124 | 1.0 | PANELS DBs Supply and Installation of main LT panel,genarally conforming to IS 8623 IS-13947 IEC-439 front operated, dead back floor mounted , totally enclosed, compartmentalised, vermin proof,indoor, non-drawout type,power panel, fabricated out of 2 1.6mm thick CRCA sheets, fully powder coated after seven tank treatment, having gasketed hinged cover on each cubicle with insulated door knob, incorporating horizontal and vertical copper busbars complete with all internal wiring, danger sign board, earth-bus and lugs, cable chamber, busbar chamber,aluminium anodized name plates etc.as required, including 2 nos. of 6 dia instrument cooling fan with switch and ventilation louvres with wire mesh,housing below mentioned switchgears meters. 9W fitting with CFL lamp, switch shall be provided in each vertical section, (Panel should conform to Form- 3b of IEC- 439) (GA drawing of the panel to be got approved from the Consultant before taking up fabrication and all panels to be factory inspected before despatch) Notes 1. All MCCBs shall have rotary handle 2. All MCCBs shall have phase spreader assembly onboth Line Load ends. 3. All MCCB shall have Minimum Ics=Icu4. Incomer shall have auxilliary ON OFF TRIP status contacts and the same shall be wired upelectronic trip setting to Metering Compartment)5. The panel shall conform to Form-3b as per IEC-4396. All MCCB to be of Schneider ABB make7. All MCCB to be current limiting type, LSIG 8. Incomer MCCB to be shunt trip facility7. With DOL Starter 5.5KW 7.5KW for air washer exhaust fan8. With VFD for 5.5KW 7.5KW for air washer exhaust fan make Selec9.Please provide CO2,FM200 HFC-227ea gas based automatic tube detection suppression system needs to be installed in Electrical Panel |  | 0.00 | 0.00 |  | 0
149125 | 1.1.1 | MAIN PANEL | Set | 0.00 | 1.00 |  | 343000
149126 | 1.2 | Suply and installation of Four -Tier, Multi-Way, TPN, Distribution Board for Lighting Power distribution, surface mounted on wall, sheet metal fabricated,powder coated, having dust-proof and vermin proof, gasketed and hinged acrylic door with all internals such as DIN rails, neutral-link, interconnected wiring complete with earthing lugs housing switchgears (IP-43 with Metal Door) Refer SLD DB Schedule (Make Legrand-Ekinoxe Schneider) |  | 0.00 | 0.00 |  | 0
149127 | 1.2.1 | KITCHEN DB 1 (12WAY TPN) | Set | 0.00 | 1.00 |  | 29600
149128 | 1.2.2 | KITCHEN DB 2 (8WAY TPN) | Set | 0.00 | 1.00 |  | 27500
149129 | 1.2.3 | LPDB 1 (12WAY TPN) | Set | 0.00 | 1.00 |  | 29600
149130 | 1.2.4 | UPS OUTPUT | Set | 0.00 | 1.00 |  | 7000
149131 | 1.2.4 | UPSDB (16WAY SPN) | Set | 0.00 | 1.00 |  | 11350
149132 | 1.4 | S I of 32A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 0.00 | 1.00 |  | 5000
149133 | 1.5 | S I of 32A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 0.00 | 1.00 |  | 5000
149134 | 1.6 | S I of 40A, TP, MCB + 415 V, in powder coated sheet metal box for terminating UPS to UPS DB etc. | Nos | 0.00 | 2.00 |  | 5500
149135 | 1.10 | S I of 32A,TP ELMCB 300mA, Metal clad,Power socket in powder coated metal box for supplying power to AC etc. IP65 | Nos | 0.00 | 2.00 |  | 7000
149136 | 2.0 | CABLES |  | 0.00 | 0.00 |  | 0
149137 | 2.1 | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts laid in ground laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications. |  | 0.00 | 0.00 |  | 0
149138 | 2.1.1 | 3.5C x 120 Sq.mm. AL Cable- MAIN PANEL | R.M | 0.00 | 20.00 |  | 1205
149139 | 2.1.6 | 3.5C x 25 Sq.mm. AL Cable | R.M | 0.00 | 10.00 |  | 290
149140 | 2.1.7 | 4C x 16 Sq.mm. CU Cable - KPDB1 2 | R.M | 0.00 | 20.00 |  | 1265
149141 | 2.1.8 | 4C x 10 Sq.mm. CU Cable - Kitchen Equipments | R.M | 0.00 | 40.00 |  | 955
149142 | 2.1.9 | 4C x 6 Sq.mm. CU Cable - LPDB, COLD ROOM, FRESH AIR EXHAUST | R.M | 0.00 | 80.00 |  | 725
149143 | 2.1.10 | 4C x 4 Sq.mm. CU Cable - DUCTABLE UNIT | R.M | 0.00 | 50.00 |  | 495
149144 | 2.1.11 | 4C x 2.5 Sq.mm. CU XLPE Cable | R.M | 0.00 | 10.00 |  | 287
149145 | 2.1.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | R.M | 0.00 | 50.00 |  | 501
149146 | 2.1.15 | 3C X 4sq.mm CU Cable - DUCTABLE UNIT | R.M | 0.00 | 40.00 |  | 380
149147 | 2.1.16 | 3C x 2.5 Sq.mm. CU Cable | R.M | 0.00 | 20.00 |  | 250
149148 | 2.1.21 | 2C X 2.5sq.mm CU Cable | R.M | 0.00 | 20.00 |  | 150
149149 | 2.1.22 | 5C X 2.5sq.mm CU Cable - LCS | R.M | 0.00 | 20.00 |  | 570
149150 | 2.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
149151 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
149152 | 2.2.1 | 3.5C x 120 Sq.mm. AL Cable- MAIN PANEL | Nos | 0.00 | 2.00 |  | 1205
149153 | 2.2.6 | 3.5C x 25 Sq.mm. AL Cable | Nos | 0.00 | 2.00 |  | 290
149154 | 2.2.7 | 4C x 16 Sq.mm. CU Cable - KPDB1 2 | Nos | 0.00 | 4.00 |  | 1265
149155 | 2.2.8 | 4C x 10 Sq.mm. CU Cable - Kitchen Equipments | Nos | 0.00 | 4.00 |  | 955
149156 | 2.2.9 | 4C x 6 Sq.mm. CU Cable - LPDB, COLD ROOM, FRESH AIR EXHAUST | Nos | 0.00 | 8.00 |  | 725
149157 | 2.2.10 | 4C x 4 Sq.mm. CU Cable - DUCTABLE UNIT | Nos | 0.00 | 2.00 |  | 495
149158 | 2.2.11 | 4C x 2.5 Sq.mm. CU XLPE Cable | Nos | 0.00 | 2.00 |  | 287
149159 | 2.2.13 | 3C x 16 Sq.mm. CU able | Nos | 0.00 | 4.00 |  | 1025
149160 | 2.2.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | Nos | 0.00 | 4.00 |  | 501
149161 | 2.2.15 | 3C X 4sq.mm CU Cable - DUCTABLE UNIT | Nos | 0.00 | 4.00 |  | 380
149162 | 2.2.16 | 3C x 2.5 Sq.mm. CU Cable | Nos | 0.00 | 2.00 |  | 250
149163 | 2.2.21 | 2C X 2.5sq.mm CU Cable | Nos | 0.00 | 5.00 |  | 150
149164 | 2.2.22 | 5C X 2.5sq.mm CU Cable - LCS | Nos | 0.00 | 4.00 |  | 570
149165 | 3.0 | POINT WIRING |  | 0.00 | 0.00 |  | 0
149166 | 3.1 | LIGHT POINTSub mains Pre-Primary wiring i.e. from DB to room switch board shall be carried out for Pre-primary point using 2.5 sqmm copper stranded. All lighting fixture, wiring shall be carried out for primary point using 2.5 sqmm copper stranded for secondary wiring 1.5sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduits (including flexible conduits for drops to light fittings) . Individual junction inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12-8 points 800 watts as per following configuration (LDBs located at two locations as shown) (The Switch Socket cost shall be paid separately.)From distribution board to switch board will be termed as Pre-primary point, average wiring length for Pre-primary point to be considered as 15 metres. From switch board to first light fitting and switch board to switch board will be termed as primary point, average wiring length for primary point to be considered as 6 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 4 metres. Light point wiring shall be included submains wiring from D.B. to room switch board. Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
149167 | 3.1.1 | Pre-Primary point (sub mains point) | Nos | 0.00 | 20.00 |  | 4000
149168 | 3.1.2 | Primary point | Nos | 0.00 | 15.00 |  | 3500
149169 | 3.1.3 | Secondary Point | Nos | 0.00 | 90.00 |  | 2100
149170 | 3.3 | Power Point (Utility) |  | 0.00 | 0.00 |  | 0
149171 |  | Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 2.5 sqmm copper stranded. Secondary wiring 2.5sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduit . Individual junction inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket. |  | 0.00 | 0.00 |  | 0
149172 |  | From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 15 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 6 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point. |  | 0.00 | 0.00 |  | 0
149173 |  | Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
149174 | 3.3.1 | Primary point | Nos | 0.00 | 12.00 |  | 4400
149175 | 3.3.3 | Secondary Point | Nos | 0.00 | 22.00 |  | 1400
149176 | 3.4 | Power Point (Kitchen BAR) |  | 0.00 | 0.00 |  | 0
149177 |  | Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 4 sqmm copper stranded. Also used 3R x 2.5sqmm copper stranded. Secondary wiring 4 sqmm copper stranded conductor 660 1100V grade PVC FRLS insulated wire in GI Conduit . Individual junction inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket. |  | 0.00 | 0.00 |  | 0
149178 |  | From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 22 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 1 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point. |  | 0.00 | 0.00 |  | 0
149179 |  | Note Length may vary as per actual site condition. Vendor shall be crossverify before bidding. |  | 0.00 | 0.00 |  | 0
149180 | 3.4.1 | Primary point | Nos | 0.00 | 30.00 |  | 5200
149181 | 3.5 | S I of GI Conduits including all accessories, clamps, spacers, bends, tee, cross etc. as required at site for miscellaneous use in following sizes |  | 0.00 | 0.00 |  | 0
149182 | 3.5.2 | 25mm dia | Mtr | 0.00 | 170.00 |  | 265
149183 | 3.6 | S I of flexible GI Conduits including all accessories, clamps, spacers, end adopters (Glands) etc. as required at site in following sizes |  | 0.00 | 0.00 |  | 0
149184 | 3.6.2 | 25mm dia (COMMON) | Mtr | 0.00 | 110.00 |  | 70
149185 | 3.7 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular shuttered type switch socket outlets with modular front plate, on Suitable MS box, G.I. back box and all required accessories etc. Supply Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw wall plugs and other necessary hardware, marking identification numbers of circuits interconnections of the switch sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND |  | 0.00 | 0.00 |  | 0
149186 | 3.7.1 | 6A One way plate type switch | Nos | 0.00 | 10.00 |  | 142
149187 | 3.7.4 | 6A SOCKET SWITCH FOR UPS POWER +DATA | Nos | 0.00 | 1.00 |  | 1300
149188 | 3.7.5 | 3no. 6A SOCKET SWITCH FOR UPS POWER +3nos DATA | Nos | 0.00 | 2.00 |  | 4000
149189 | 3.7.6 | 5no. 6A SOCKET SWITCH FOR UPS POWER +5nos DATA | Nos | 0.00 | 1.00 |  | 4600
149190 | 3.7.7 | 4no. 6A SOCKET SWITCH FOR UPS POWER + 4nos. DATA | Nos | 0.00 | 1.00 |  | 4350
149191 | 3.7.8 | 2no. 6A SOCKET SWITCH FOR UPS POWER + 2nos. DATA | Nos | 0.00 | 6.00 |  | 3600
149192 | 3.7.9 | 6A SOCKET SWITCH FOR POWER | Nos | 0.00 | 14.00 |  | 800
149193 | 3.7.10 | 6 16A SOCKET SWITCH POWER | Sets | 0.00 | 2.00 |  | 900
149194 | 3.7.11 | 6 16A SOCKET SWITCH POWER-KITCHEN | Sets | 0.00 | 30.00 |  | 900
149195 | 3.7.12 | 6 16A SOCKET SWITCH POWER-GEYSER | Sets | 0.00 | 2.00 |  | 900
149196 | 3.7.13 | 6 16A SOCKET SWITCH POWER-HAND DRYER | Sets | 0.00 | 1.00 |  | 900
149197 | 3.7.14 | 1PHASE - 20A INDUSTRIAL TYPE SOCKET | Nos | 0.00 | 1.00 |  | 3200
149198 | 3.7.15 | 3PHASE - 20A INDUSTRIAL TYPE SOCKET | Nos | 0.00 | 1.00 |  | 12000
149199 | 3.7.16 | 3PHASE - 63A INDUSTRIAL TYPE SOCKET + DATA | Nos | 0.00 | 1.00 |  | 14000
149200 | 3.7.17 | 6 16A SOCKET SWITCH FOR TV DMB + DATA | Nos | 0.00 | 2.00 |  | 1050
149201 | 3.7.18 | EXIT SIGNAGE | Nos | 0.00 | 2.00 |  | 1500
149202 | 3.7.19 | OUTDOOR SIGNAGE | Nos | 0.00 | 1.00 |  | 2000
149203 | 3.7.20 | DIGITAL SCREEN | Nos | 0.00 | 2.00 |  | 1900
149204 | 3.7.21 | data cum telephone back GI BACK box 2”x2” suitable for data socket | Nos | 0.00 | 4.00 |  | 120
149205 | 3.7.22 | 5 Pin Industrial Socket (3 PHASE) | Nos | 0.00 | 2.00 |  | 12000
149206 | 3.7.23 | 3 Pin Industrial Socket (1 PHASE) | Nos | 0.00 | 15.00 |  | 3200
149207 | 4.4 | S I of 1 Run x 25mm dia, GI Conduit in Floor. | Mtr | 0.00 | 120.00 |  | 265
149208 | 4.7 | S I of floor junction boxes similar to above but size 150mm x 150mm x 60 mm | Nos | 0.00 | 10.00 |  | 310
149209 | 4.8 | S I of GI Pregalvanizd Perforated type Cable Tayof following sizes suspended from ceiling or fixedvertically on wall column as per route directed at site including all necessary bends, tees, crosses and alsoincluding all necessary supporting arrangement.All supporting hardware including nuts, bolts etc. shall be also of galvanised M.S. as approved(PROFAB INDIANA ASIAN approved equivalent) |  | 0.00 | 0.00 |  | 0
149210 | 4.8.1 | 100mm x 50mm x 1.6mm | Mtr | 0.00 | 12.00 |  | 366
149211 | 4.8.2 | 300mm x 50mm x 1.6mm | Mtr | 0.00 | 20.00 |  | 1332
149212 | 5.0 | LIGHT FIXTURES INSTALLATION Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect consultant at site. |  | 0.00 | 0.00 |  | 0
149213 | 5.1.1 | 600mm X 600mm DROP IN LED CEILING LIGHT | Nos | 0.00 | 7.00 |  | 500
149214 | 5.1.2 | BOH 600mm LONG SURFACE MOUNTED EMERGENCY LIGHT | Nos | 0.00 | 3.00 |  | 500
149215 | 5.1.3 | 4 FT (2 TUBE) KB53 LIGHT | Nos | 0.00 | 4.00 |  | 300
149216 | 5.1.5 | HEAT LAMPS | Nos | 0.00 | 4.00 |  | 300
149217 | 5.1.6 | WARM WHITE DOWNLIGHT -L2 | Nos | 0.00 | 16.00 |  | 200
149218 | 5.1.7 | WARM WHITE DOWNLIGHT -L3 | Mtr | 0.00 | 7.00 |  | 500
149219 | 5.1.8 | WARM WHITE DOWNLIGHT -L4 | Nos | 0.00 | 4.00 |  | 500
149220 | 5.1.9 | WARM WHITE DOWNLIGHT -L5 | Nos | 0.00 | 6.00 |  | 500
149221 | 5.1.10 | WARM WHITE DOWNLIGHT -L6 | Nos | 0.00 | 1.00 |  | 500
149222 | 5.1.11 | LIGHT -L7 L8 | Nos | 0.00 | 7.00 |  | 500
149223 | 6.0 | EARTHING |  | 0.00 | 0.00 |  | 0
149224 | 6.1 | S I of earth pit comprising of specially designed SEE Ashlok brand Earth Electrode system 3.00 meter long including necessary materials like side fill compound etc. as required with standard brick masonary chamber with hinged cover and watering arrangement model SEE-60 C with SFC-20 Equivalent ASHLOK MODEL T39 HD (50MM DIA. 3 MTR) | Nos | 0.00 | 2.00 |  | 19150
149225 | 6.2 | S I of copper GI earthing wires strips in following sizes |  | 0.00 | 0.00 |  | 0
149226 | 6.3 | 8 SWG GI bare wire | Mtr | 0.00 | 135.00 |  | 40
149227 | 6.4 | 8 SWG CU bare wire | Mtr | 0.00 | 40.00 |  | 80
149228 | 6.6 | 25mm x 6mm thick GI strip welded painted green | Mtr | 0.00 | 30.00 |  | 170
149229 | 6.7 | S I of isolated dedicated earthing grounding system for computers etc.using insulated green-yellow copper earthing wire laid fixed bare on wall ceiling from separately made earth pit to the equipment in following sizes The rate shall include termination also. |  | 0.00 | 0.00 |  | 0
149230 | 6.7.1 | 6 Sqmm copper, yellow-green green insulation | Mtr | 0.00 | 20.00 |  | 132
149231 | 6.8 | S I of Main bus for isolated earth comprising of 300mm x 25 mm x 3mm thick Tinned copper bar fixed on insulated support and having 10 nos of holes and nut bolts studs for clamping the earth leads,all contained in MS PVC box and having transparent acrylic cover as approved by the consultant | Nos | 0.00 | 1.00 |  | 2805
149232 | 7.1 | Supply Install. Of RG 6 TV Cable in 25mm GI Conduit | Mtr | 0.00 | 40.00 |  | 262
149233 | 7.2 | Supply Laying of RG11 use for Main Cable TV | Mtr | 0.00 | 80.00 |  | 305
149234 | 8 | DATA DISTRIBUTION |  | 0.00 | 0.00 |  | 0
149235 | 8.5 | Supply Installation of I O DATA Outlet (RJ-45) | nos | 0.00 | 43.00 |  | 555
149236 | 8.6 | S I of Installation of Wi-Fi ceiling mounted Access Point, managed by controller software | nos | 0.00 | 3.00 |  | 0
149237 | 8.8 | CABLES |  | 0.00 | 0.00 |  | 0
149238 | 8.8.3 | Supply providing of CAT 6 UTP cables in the laid raceways Conduits including terminations | mtr | 0.00 | 516.00 |  | 127
149239 | 8.8.4 | Patch cord (2 mtr-user end) | Each | 0.00 | 20.00 |  | 0
149240 | 8.9 | Supply, Installation, Testing Commissioning of Velcro Ties ( 22 Mtrs = 1 Roll) | Nos | 0.00 | 1.00 | qty in roll | 0
149241 | 8.10. | Supply, Installation, Testing Commissioning of Cable Ties 200mm ( 100 Nos. Pkt) | Nos | 0.00 | 1.00 | Qty in pkt | 0
149242 | 8.11 | Project Management including Freight Forwarding, Cable Bunching, Printed Numbering, tube type Ferruling both sides, Face plate, Patch panel patch cords both sides, Documentation etc.. | Job | 0.00 | 1.00 |  | 0
149243 | 8.12 | Supplying and fixing 15U Rack Aluminium Frame - 600x600mm with 4 x FAN, Dual Split perforated Door at Front and Back Side, 2 x Vertical Cable Basket, 2 x 12 socket 5 15A PDU with MCB, side Panels of 2 nos and Heavy Duty Castors with break, 19 Reduced Channel - Loop Type (DATA+CCTV) | Job | 0.00 | 1.00 |  | 0
149244 | 8.13 | Supply installation of GI Conduits with junction boxes, reducer etc. complete concealed surface mounting as required. |  | 0.00 | 0.00 |  | 0
149245 | 9.0 | SUPPLY INSTALLATION OF SAFETY ITEMS |  | 0.00 | 0.00 |  | 0
149246 | 9.3 | Caution boards (415V) of std. Size | Nos | 0.00 | 1.00 |  | 333
149247 | 9.4 | Rubber mat at panel room 12mm thk. 1mtr. Wide | mtr | 0.00 | 1.00 |  | 3025
149248 | 9.5 | Shock treatment chart as per electricity board | Nos | 0.00 | 1.00 |  | 1705
149249 | 10.0 | UPS INVERTER System |  | 0.00 | 0.00 |  | 0
149250 | 10.1 | Supply, Installation, testing and commissioning of 6 KVA UPS System Single Phase I C Single Phase O G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings the specifications. Make Emerson APC Consul Neowatt Vivtar Electronics | set | 0.00 | 1.00 |  | 180000
149251 | 11.0 | CCTV |  | 0.00 | 0.00 |  | 0
149252 | 11.10 | Supply Installation of CAT-6 Cable for Camera Signal | mtr | 0.00 | 20.00 |  | 127
149253 | 11.11 | Supply Installation of 3+1 Cable for CCTV | mtr | 0.00 | 300.00 |  | 110
149254 | 12.0 | PA SYSTEM |  | 0.00 | 0.00 |  | 0
149255 | 12.1 | Supply Installation of 6W Ceiling Speaker with box | RM | 0.00 | 9.00 |  | 0
149256 | 12.2 | Control Unit (with volume and on off switch) (Smooth stepless control, but the control shall be through dimmer switch, the make of which will be same as the make of light control switches) | nos | 0.00 | 1.00 |  | 0
149257 | 12.3 | Supply Installation of 120W Booster Amplifier | nos | 0.00 | 1.00 |  | 0
149258 | 12.4 | Installation of 2 core 2.5 Sq.mm PVC insulated twisted copper conductor Speaker wires as required. | RM | 0.00 | 80.00 |  | 132
149259 |  | BOQ for temperory power connection |  | 0.00 | 0.00 |  | 0
149260 | 1 | Supply Installation of 4 Way TPN DB Incomer - 32A FP RCBO 30MA- 1 Nos Outgoing -10 16A SP MCB-12 NOS | Nos | 0.00 | 1.00 |  | 18500
149261 | 2 | Supply Installation of 3 Phase Energy Meter - KVAH meter - Make L T, Schneider, Siemens, HPL, ABB CG | Nos | 0.00 | 1.00 |  | 9250
149262 | 3 | Supply Laying of 4C x 4 Sq mm Cu Armoured Cable | Mtrs | 0.00 | 30.00 |  | 495
149263 | 4 | Supply Laying of 3C x 2.5 Sq mm Cu Flexible lead wire | Mtrs | 0.00 | 20.00 |  | 235
149264 | 5 | Supply Installation of 40W Led Light Fixture | Nos | 0.00 | 10.00 |  | 1735