## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
163338 | 1.1 | DISTRIBUTION BOARDs Supplying, Installation, Testing Commissioning of following size of recessed type wall mounted Double door (IP 43 protection) made out of 16 gauge (1.5 mm thick) M.S. sheet i c. powder coated painting, interconnections with supply fixing with the following accessories etc. as required. 8 way VTPN DB-1 Incomer 125A, 4P MCCB with inbuilt O L, S C and Earth Fault - 1 No BUSBAR Neutral links suitable for 8 way TPN DB 3 Nos. OUTGOING 6 - 32 Amp. SP MCB C Curve 24 Nos. | Set | 0.00 | 1.00 | MCB only 6x3 = 18 Nos provide by client Testing and Commissioning to br done | 42000
163339 | 1.2 | DISTRIBUTION BOARDs Supplying, Installation, Testing Commissioning of following size of recessed type wall mounted Double door (IP 43 protection) made out of 16 gauge (1.5 mm thick) M.S. sheet i c. powder coated painting, interconnections with supply fixing with the following accessories etc. as required. 12 way TPN DB- LDB INCOMING 40 Amp 4 Pole MCB ( 10 kA) 1 No. BUSBAR Neutral links suitable for 12 way TPN DB 3 Nos. OUTGOING 40 Amp DP RCCB ( 30 mA) 3 Nos. 6 - 32 Amp. SP MCB C Curve 30 Nos. | Set | 0.00 | 1.00 | Materil are available - Earthing Works - to be done Testing and Commissioning to be done | 26000
163340 | 1.3 | DISTRIBUTION BOARDs Supplying, Installation, Testing Commissioning of following size of recessed type wall mounted Double door (IP 43 protection) made out of 16 gauge (1.5 mm thick) M.S. sheet i c. powder coated painting, interconnections with supply fixing with the following accessories etc. as required. 12 way TPN DB- PDB INCOMING 63 Amp 4 Pole MCB ( 10 kA) 1 No. BUSBAR Neutral links suitable for 12 way TPN DB 3 Nos. OUTGOING 63 Amp DP RCCB ( 30 mA) 3 Nos. | Set | 0.00 | 1.00 | Materil are available - Earthing Works - to be done Testing and Commissioning to be done | 26000
163341 | 1.4 | DISTRIBUTION BOARDs Supplying, Installation, Testing Commissioning of following size of recessed type wall mounted Double door (IP 43 protection) made out of 16 gauge (1.5 mm thick) M.S. sheet i c. powder coated painting, interconnections with supply fixing with the following accessories etc. as required. 16 way SPN DB UPS DB-U INCOMING 63 Amp 2Pole MCB ( 10 kA) 1 No. BUSBAR Neutral links suitable for 12 way SPN DB 1 Nos. OUTGOING 63 Amp DP RCCB ( 30 mA) 1 Nos. 6 - 20 Amp. SP MCB D Curve 12 Nos. | Set | 0.00 | 1.00 | Materil are available - Earthing Works - to be done Testing and Commissioning to be done | 16000
163342 | 2 | LIGHT POWER POINT WIRING |  | 0.00 | 0.00 |  | 0
163343 | 2.1 | Point wiring for DB controlled primary light points wall fan exhaust fan with 3x2.5sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, including circuit wiring, in recessed surface ISI marked 1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work complete as per specifications and as required. This item includes the Switch, face plate and zinc chromate passivated MS Box.(cost of MCB included in DB) | Nos | 0.00 | 25.00 | PVC Conduits to be Removed and MS Conduits to be done., by using the Same Cables. | 4500
163344 | 2.2 | Point wiring for Secondary light points wall fan ceiling fan exhaust fan with 3x2.5sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, including circuit wiring, in recessed surface ISI marked1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work complete as per specifications and as required. | Nos | 0.00 | 65.00 | PVC Conduits to be Removed and MS Conduits to be done., by using the Same Cables. May Cause damage to existing Cladding and Flooring | 3000
163345 | 2.3 | Point wiring for a 5Pin 6A 240 volt Primary universal switch socket outlet with 3x2.5sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, including circuit wiring, in recessed surface ISI marked 1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work and including the cost of supplying and fixing modular face plate mounted 5 pin 6 amp 240 volt combined shuttered socket outlet alongwith 6 amp 240 volt control switch housed in a zinc chromate passivated MS box with molded cover plate complete as per specifications and as required (Raw + UPS) | Nos | 0.00 | 6.00 | PVC Conduits to be Removed and MS Conduits to be done., by using the Same Cables. | 5500
163346 | 2.4 | Point wiring for a 5Pin 6A 240 volt Secondary (Loop Point) universal switch socket outlet (3 outlets wired on 1 circuit) with 3x2.5sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, including circuit wiring, in recessed surface ISI marked 1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work and including the cost of supplying and fixing modular face plate mounted 5 pin 6 amp 240 volt combined shuttered socket outlet alongwith 6 amp 240 volt control switch housed in a zinc chromate passivated MS box with molded cover plate complete as per specifications and as required (Raw + UPS) | Nos | 0.00 | 22.00 |  | 3500
163347 | 2.6 | Point wiring for a 6 pin 16A 240volt Switch socket outlet , with 3x4.0sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, in recessed surface ISI marked 1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 6 pin 240 volt 16 amp combined shuttered socket outlet alongwith 16 amp 240 volt control switch housed in a zinc chromate passivated MS box complete as per specifications and as required.(Primary Point) | Nos | 0.00 | 21.00 |  | 6500
163348 | 2.7 | Point wiring for a 6 pin 16A 240volt Switch socket outlet , with 3x4.0sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, in recessed surface ISI marked 1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 6 pin 240 volt 16 amp combined shuttered socket outlet alongwith 16 amp 240 volt control switch housed in a zinc chromate passivated MS box complete as per specifications and as required.(Loop Point ( One Socket loop in one Ckt. )) | Nos | 0.00 | 9.00 |  | 3500
163349 | 2.8 | Point wiring for a 6 pin 16A 240volt Switch socket outlet , with 3x6.0sqmm (P+N+E) FRZHS PVC insulated 660 1100 volt grade stranded copper conductor wires, in recessed surface ISI marked 1.6mm thick 25mm dia MS Conduit including the cost of cutting making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 6 pin 240 volt 16 amp combined shuttered socket outlet alongwith 16 amp 240 volt control switch housed in a zinc chromate passivated MS box complete as per specifications and as required.(Geyzer + RO Point + Pump) | Nos | 0.00 | 4.00 |  | 7000
163350 |  | KITCHEN EQUIPMENT POINT WIRING. |  | 0.00 | 0.00 |  | 0
163351 | 2.9 | Wiring for 240 volts single phase and neutral 20 25Amps Metal clad 3 pin socket outlet in factory fabricated powder coated metal box with 20 25A DP MCB and plug top with 2x4sqmm + 1x2.5sqmm (Earth) 3rd pin box earthing in FRLS PVC insulated 660 1100 volt grade stranded FRZH copper conductor including wire, ISI marked 1.6mm thick 25 dia. recessed or surface MS conduit including the cost of cutting making good chases in brick work etc complete..(IP 67) | Nos | 0.00 | 3.00 |  | 7500
163352 | 2.12 | Wiring for 415 volts Three Phase and neutral 32A industrial 5pin socket outlet in factory fabricated powder coated PVC box with 32A FP MCB and plug top with 4x6sqmm+2x4sqmm (Earth) 5th pin box earthing in PVC insulated 660 1100 volt grade stranded FRZHS copper conductor wires, ISI marked1.6mm thick 50 dia. recessed or surface MS conduit including the cost of cutting making good chases in brick work etc complete ..(IP 67) | Nos | 0.00 | 2.00 | Connectivity to be Check and installtion to be done | 18000
163353 |  | LIGHT FIXTURES AND FITTINGS |  | 0.00 | 0.00 |  | 0
163354 |  | Provinding Installation, connecting, testing and commissioning of the following light fixtures complete with housing, reflectors, all accessories i.e. copper wound Electronic ballast, HPF condensers, starters, holders, hanging fixing arrangements etc. complete as required - For detailed specification please refer RCP |  | 0.00 | 0.00 |  | 0
163355 |  | 72W, Suspended Linear Light(C1) | Nos | 0.00 | 1.00 | Only Installation | 500
163356 |  | 36W, Suspended Linear Light(C1) | Nos | 0.00 | 1.00 | Only Installation | 1000
163357 |  | 38 W 595X595 Mm Ceiling Led Light(C2) | Nos | 0.00 | 4.00 | Only Installation | 1000
163358 |  | 15W,Mini TL2 line(C4) | Nos | 0.00 | 8.00 | Only Installation | 500
163359 |  | 15W ,Recessed cob downlight(C5) | Nos | 0.00 | 10.00 | Only Installation | 1000
163360 |  | 30W ,Pendent LED Vertica LED(C6) | Nos | 0.00 | 21.00 | Only Installation | 500
163361 |  | 36W Hanging Light(C7) 3 NOS -108 WATT | Nos | 0.00 | 15.00 | Only Installation | 1000
163362 |  | 120W Decorative Light(C8) SET OF 3 | Nos | 0.00 | 8.00 | Only Installation | 500
163363 |  | Strip Light | Mtr. | 0.00 | 50.00 | Only Installation | 100
163364 | 4 | ELECTRICAL CABLE CABLE TRAY RACEWAY EARTHING |  | 0.00 | 0.00 |  | 0
163365 | 4.1 | Supply laying testing and commissioning of following sizes of XLPE insulated PVC sheathed aluminium copper conductor armoured cable of 1.1 KV grade on existing cable tray surface including saddle, clamps etc. complete as required. |  | 0.00 | 0.00 |  | 0
163366 |  | 4C x 50 Sq.mm, Al | Rm | 0.00 | 50.00 |  | 600
163367 |  | 4C x 16 Sq.mm, Cu | Rm | 0.00 | 10.00 |  | 1150
163368 |  | FIRE DETECTION AND ALARM SYSTEM |  | 0.00 | 0.00 |  | 0
163369 |  | Supply, installation, testing and commissioning of Manual Call Points Addressable Type, flush monted in partition or concealed in wall for manual actuation in case of fire. | Nos. | 0.00 | 3.00 |  | 0
163370 |  | Supply, installation, fixing, testing and commissioning of Strobe Lights Cum Hooter with 110 cd. The strobes shall be synchronized for better evacuation. | Nos. | 0.00 | 3.00 |  | 0
163371 |  | Supply, installation, testing and commissioning of response indicators suitable for above smoke detector complete with M.S. junction box top hylum sheet and required accessories. | Nos. | 0.00 | 7.00 |  | 0
163372 |  | Supplying and fixing of following sizes of MS conduit alongwith the accessories in surface recess including cutting the wall and making good the same in case of recessed conduit as required. |  | 0.00 | 0.00 |  | 0
163373 |  | 25 mm dia MS conduit | RM | 0.00 | 80.00 |  | 210
163374 |  | 20 mm dia PVC flexible conduit | RM | 0.00 | 30.00 |  | 60
163375 |  | UPS INVERTER SYSTEM Supply ,Installation and commossioing of 5 KVA Single phase input (220 V + 15%), Single phase output (220 V + 10%) on line UPS with inbuilt isolation Transformer complete with 17 18Ah 4Nos. maintenence Free battery with battery rack. External battery backup should be min. 30 minutes. complete with wheel, internal wiring, connection, termination etc all accessories as required. | No | 0.00 | 1.00 |  | 175000