## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
88131 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING |  | 0.00 | 0.00 |  | 0
88132 |  | If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  | 0.00 | 0.00 |  | 0
88133 | B | DRAINAGE SYSTEM |  | 0.00 | 0.00 |  | 0
88134 |  | INTERCEPTORS SEPERATORS |  | 0.00 | 0.00 |  | 0
88135 | B.1.1 | Installing, Testing Commissioning of Greese Trap or Grease Interceptor (Above Ground floor) of 304 grade stainless steel material with interceptor body, preforated bucket, baffles, integral trap, inlet outlep pipe sleeve and stainless steel interceptor cover of approved make and with all necessary fittings connectors etc. (Make Nugreen , Kessel and Concessionaire can propose another make in SS material.)NGT 50 - Flow Rate (2.20 LPS 132 LPM) | Nos | 0.00 | 1.00 |  | 42000
88136 |  | VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
88137 | B.2 | Supplying, Installing, Testing Commissioning of ABS Air Admittance Valve conforming to EN 12380, with an air admittance air flow rate of 6.1 L s and a temperature range of operation from -20 C to + 60 C of approved make with all necessary adapters, fittings and connectors etc. (Make Astral Supreme for Pipe and Fittings) |  | 0.00 | 0.00 |  | 0
88138 | B.2.1 | 32 mm Dia | Nos | 0.00 | 1.00 |  | 6500
88139 |  | DRAINS, TRAPS CLEANOUTS |  | 0.00 | 0.00 |  | 0
88140 | B.4 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 350 X 350 mm, lateral horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make Custom made) |  | 0.00 | 0.00 |  | 0
88141 | B.4.1 | 50 mm Dia - Outlet | Nos | 0.00 | 4.00 |  | 9500
88142 | B.5 | Supplying, Installing, and testing of uPVC P Trap (self-cleaning type) with odor water seal trap of approved make with all necessary adapters, fittings and connectors, etc. |  | 0.00 | 0.00 |  | 0
88143 | B.5.1 | 32 mm Dia Outlet | Nos | 0.00 | 6.00 |  | 1800
88144 | B.6 | Supplying, Installing Testing of cast iron Floor Trap (150 mmx 150 mm) with Stainless Steel slotted top cover, odour water seal trap of approved make with all necessary adapters, fittings and connectors etc. (Makes NECO or equivalent with Airport approval) |  | 0.00 | 0.00 |  | 0
88145 | B.6.1 | 75 mm Dia - Outlet | Nos | 0.00 | 1.00 |  | 2850
88146 |  | DRAINAGE SYSTEMS PIPING |  | 0.00 | 0.00 |  | 0
88147 | B.7 | Supplying, Installing, Testing, and Commissioning of uPVC Pipe, for drainage with all necessary fittings such as bends, wye s, reducers, san tee s, double wye s, double combinations, san cross, and cleanout plugs etc, of approved make. and with all necessary supports clamps for the above-raised floor pipes as per standards and site conditions requirements. (Make Astral Supreme for Pipe and Fittings) |  | 0.00 | 0.00 |  | 0
88148 | B.7.1 | 32 mm Dia | Mtr | 0.00 | 2.00 |  | 650
88149 | B.7.2 | 40 mm Dia | Mtr | 0.00 | 10.00 |  | 850
88150 | B.7.3 | 50 mm Dia | Mtr | 0.00 | 25.00 |  | 950
88151 | B.7.4 | 75 mm Dia | Mtr | 0.00 | 6.00 |  | 1050
88152 | C | WATER SUPPLY SYSTEM |  | 0.00 | 0.00 |  | 0
88153 |  | WATER SUPPLY EQUIPMENTS |  | 0.00 | 0.00 |  | 0
88154 | C.1 | Supply, Installation, Testing Commissioning of Electric Water Heater with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. and proper supports necessary as per standards and site condition requirements. (Make Ariston Racold or equivalent with Airport approval) |  | 0.00 | 0.00 |  | 0
88155 | C.1.1 | 65 Liters vertical storage water heater | Nos | 0.00 | 1.00 |  | 32000
88156 | C.2 | Supply, Installation, Testing Commissioning of RO Filteration Unit for supplying pure filtered potable water to equipments like Combi-steamers baking ovens, Fresh water taps Coolers, Coffee Espresso machines, Dish-washers, Post-mix machines, Ice-machines, and Boiling-water taps etc. with necessary prefilters, filter cartridges, manifold heads, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. Final make, model and details to be finalized by specialist vendor after examining the water test report of incoming water supply provided at site. (Make Eco Smart Livpure or equivalent with Airport approval) |  | 0.00 | 0.00 |  | 0
88157 | C.2.1 | 15 Ltrs Hr - Flow Rate | Nos | 0.00 | 1.00 |  | 24500
88158 |  | WATER SUPPLY PIPE VALVES ACCESSORIES |  | 0.00 | 0.00 |  | 0
88159 | C.3 | Supply, Installation, Testing Commissioning of Brass Ball Valve with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar of approved make and with all necessary fittings. (Makes NECO or equivalent with Airport approval) |  | 0.00 | 0.00 |  | 0
88160 | C.3.1 | 25 mm Dia | Nos | 0.00 | 2.00 |  | 3200
88161 | C.4 | Supply, Installation, Testing, and Commissioning of chrome plated Angle Valve with wall flange rosette for all plumbing equipment fixtures with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall partition as per Architectural Interior Design and as per relevant standards. (Makes NECO or equivalent with Airport approval) |  | 0.00 | 0.00 |  | 0
88162 | C.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp fixture connection) | Nos | 0.00 | 21.00 |  | 3450
88163 |  | COLD WATER SUPPLY PIPING |  | 0.00 | 0.00 |  | 0
88164 | C.5 | Supply, Installation, Testing Commissioning of (Chlorinated Poly Vinyl Chloride) CPVC Pipe conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition requirements. (Make Astral Supreme for Pipe and Fittings) |  | 0.00 | 0.00 |  | 0
88165 | C.5.1 | 15 mm Dia | Mtr | 0.00 | 16.00 |  | 750
88166 | C.5.2 | 20 mm Dia | Mtr | 0.00 | 10.00 |  | 850
88167 | C.5.3 | 25 mm Dia | Mtr | 0.00 | 13.00 |  | 950
88168 | C.6 | Supply, Installation, Testing Commissioning of Copper Pipe conforming to BS 2871 EN 1057, (continous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition requirements. (Make Manibhadra fittings or equivalent with Airport approval) |  | 0.00 | 0.00 |  | 0
88169 | C.6.1 | 15 mm Dia | Mtr | 0.00 | 10.00 |  | 2450
88170 | C.6.2 | 22 mm Dia | Mtr | 0.00 | 12.00 |  | 3450
88171 |  | PIPING THERMAL INSULATION |  | 0.00 | 0.00 |  | 0
88172 | C.7 | Supply fixing of Pipe Insulation of 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating to prevent external mechanical damage of approved make for Hot water pipe with a operating temperature range of 0°C to 100°C, Thermal conductivity (?) 0.038 W m-K @ 40°C including suitable adhesives to fix the insulation to pipe. (Make Thermax, Maxima, Fuelpac or equivalent) |  | 0.00 | 0.00 |  | 0
88173 | C.7.1 | 15 mm Dia | Mtr | 0.00 | 10.00 |  | 350
88174 | C.7.2 | 22 mm Dia | Mtr | 0.00 | 12.00 |  | 450