## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
125171 |  | AIR HANDLING UNITS (AHUs) |  | 0.00 | 0.00 |  | 0
125172 |  | Ceiling Suspended type AHUs - With Non Thermal Break Profile |  | 0.00 | 0.00 |  | 0
125173 |  | Supply, Installation, Testing and Commissioning of double skin air handling units (AHUs) each comprising of following as per the specifications |  | 0.00 | 0.00 |  | 0
125174 |  | Casing of air handling units shall be in double skin construction. Inner skin shall be constructed out of 24 gauge plain GS sheet outer skin in 24 gauge pre-plasticized GS sheet sandwiched between 25mm thick injected PU foam insulation of density not less than 40 Kg CuM and complete with inspection doors including control wiring as required. AHUs shall have access for all parts. |  | 0.00 | 0.00 |  | 0
125175 |  | Fan section complete with forward curved DIDW type centrifugal fan s, IE3, TEFC squirrel cage induction motor suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Fan outlet velocity shall not be more than 1800 FPM (9.2MPS). Fan Motor shall be VFD compatible. Fan section should be completed with 25mm thick Armasound acoustic insulation. All fans should be AMCA certified. |  | 0.00 | 0.00 |  | 0
125176 |  | Coil section with multirows deep chilled water coil of copper tube copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge stainless steel duly insulated. Face velocity across cooling coil shall not exceed 500FPM. |  | 0.00 | 0.00 |  | 0
125177 |  | Pre-Filter (EU-4) section complete with 50mm thick washable synthetic fiber filters. Velocity across the filters shall not exceed 500 FPM. |  | 0.00 | 0.00 |  | 0
125178 |  | AHUs shall be complete with suspension arrangement, it shall also include spring type vibration isolators and rubber grommets etc. to make the installation totally vibration free. AHUs shall have separate compartment for housing all valves. |  | 0.00 | 0.00 |  | 0
125179 |  | AHUs shall be provided with mixing chamber with S A F A openings with dampers as per approved shop drawing. |  | 0.00 | 0.00 |  | 0
125180 |  | Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of each AHU. |  | 0.00 | 0.00 |  | 0
125181 |  | In addition to the above, air handling units shall be provided with fire retardant flexible canvass connections made out of canvass sleeve. Sizes of air handling units shall not exceed as mentioned in the design drawings and air handling units shall conform to the design parameters mentioned in specifications. |  | 0.00 | 0.00 |  | 0
125182 |  | The Air Handling Units (AHUs) shall be of following duty parameters |  | 0.00 | 0.00 |  | 0
125183 |  | AHU No Capacity S.P Motor Rows of Area to |  | 0.00 | 0.00 |  | 0
125184 |  | (Cfm TR) (mmWG) Rating coil be fed |  | 0.00 | 0.00 |  | 0
125185 |  | (HP) |  | 0.00 | 0.00 |  | 0
125186 |  | CSAH-1 9 3600 35-36 Seating Area | Nos | 0.00 | 2.00 |  | 0
125187 |  | VARIABLE FREQUENCY DRIVES |  | 0.00 | 0.00 |  | 0
125188 |  | Supply, Installation, Testing and Commissioning of variable frequency drives for following Air Handling Units. Variable frequency drives shall be provided with necessary sensors and transmitters complete with control wiring in all respect as required and as per specifications. VFDs shall have built-in harmonic filters. The drives shall be suitable for the following motor rating. VFDs shall be housed in precoated, vandal proof enclosure with On Off Push Buttons, Phase indication lights, A M Switch and with adequate provisions for ventilation using a fan. The VFDs shall be able to receive the signals from multiple combination of duct static pressure sensors Temp. sensors and to ramp the speed of the motor.VFDs shall be suitable to take feed back and connectivity from all the DPS as mentioned below against each motor rating to facilitate averaging activity by VFD. Quoted price shall be inclusive of return air temperature sensor Pressure Sensors and necessary electrical switches including change over switch copper cabling for integration with the AHU panel. VFD panel shall be installed adjoining AHU panels for existing AHUs. Overall protection of VFDs with Panels shall be IP-54. |  | 0.00 | 0.00 |  | 0
125189 |  | (i) Sensing Range 10mm to 50 mm WG |  | 0.00 | 0.00 |  | 0
125190 |  | (ii) Output Signal 4 mA to 20 mA |  | 0.00 | 0.00 |  | 0
125191 |  | OR |  | 0.00 | 0.00 |  | 0
125192 |  | 0 V to 10 V DC |  | 0.00 | 0.00 |  | 0
125193 |  | AHU - 3600 CFM | Nos | 0.00 | 2.00 |  | 0
125194 |  | Exhust Unit - 8000 CFM | Nos | 0.00 | 1.00 |  | 0
125195 |  | TFA Unit - 5000 CFM | Nos | 0.00 | 1.00 |  | 0
125196 |  | Tube Axial Fan - 3000 CFM | Nos | 0.00 | 1.00 |  | 0
125197 |  | EXHAUST UNIT WITH DRY SCRUBBER (For Kitchen Exhaust) |  | 0.00 | 0.00 |  | 0
125198 |  | Providing Fixing Cabinet type Exhust fan unit along with Electro static dry scrubber for kitchen exhuast to be fixed before exhust blower to eliminate the polluted air which comes out from kitchen.Cleair dry scrubber provide un equal performance in removing kitchen exhaust, smoke, oil, dust, particles and order. Techanical detaila as below Casing of air handling units shall be in double skin construction. Inner skin shall be constructed out of 24 gauge plain GS sheet outer skin in 24 gauge pre-plasticized GS sheet sandwiched between 25mm thick injected PU foam insulation of density not less than 40 Kg CuM and complete with inspection doors including control wiring as required. AHUs shall have access for all parts. Fan section complete with forward curved DIDW type centrifugal fan s, IE3, TEFC squirrel cage induction motor suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Fan outlet velocity shall not be more than 1800 FPM (9.2MPS). Fan Motor shall be VFD compatible. Fan section should be completed with 25mm thick Armasound acoustic insulation. All fans should be AMCA certified. Cabinet - 1.2mm welded mild steel sheet Finish - Powder coated |  | 0.00 | 0.00 |  | 0
125199 |  | Air Flow - 8000 CFM ESP - 35MM Air Flow Type - Horizontal standard Installation type - Ceiling Suspended Construction to be closed from top and bottom with a basin for collection drain The pre-filter retains the large particles The particles in the airflow are charged P N by the ionizing section Capacity Efficiency -Up to 99% Prefilter -Aluminum Mesh, Washable Electrical Rating -Input Power 220~240W,, 50~60Hz. Make Bry Air | Nos | 0.00 | 1.00 |  | 0
125200 |  | Treated Fresh Air Unit ( TFA Unit) - CHW Type |  | 0.00 | 0.00 |  | 0
125201 |  | Supply, Installation, Testing and Commissioning of double skin Treated Fresh Air units ceiling suspended type each comprising of following as per the specifications |  | 0.00 | 0.00 |  | 0
125202 |  | Casing of TFA units shall be in double skin construction with thermal break Aluminium profle section. Inner skin shall be constructed out of 24 gauge plain GS sheet outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg CuM and complete with inspection doors including control wiring as required. AHUs shall have access for all parts. |  | 0.00 | 0.00 |  | 0
125203 |  | Fan section complete with forward curved DIDW type centrifugal fan s, IE3, TEFC squirrel cage induction motor suitable to operate on 415+10%V, 50Hz, 3 phase AC power supply and belt drive package. Fan outlet velocity shall not be more than 1800 FPM (9.2MPS). Fan Motor shall be VFD compatible. Fan section should be completed with 25mm thick. Armasound acoustic insulation. All fans should be AMCA certified. |  | 0.00 | 0.00 |  | 0
125204 |  | Coil section with multirows deep chilled water coil of copper tube copper header and aluminium fins construction having wall thickness of tubes not less than 0.5mm. Drain pan shall be made out of 18 gauge stainless steel duly insulated. Face velocity across cooling coil shall not exceed 500FPM. |  | 0.00 | 0.00 |  | 0
125205 |  | Pre-Filter section complete with 50mm thick washable synthetic fibre filters. Velocity across the filters shall not exceed 450 FPM. |  | 0.00 | 0.00 |  | 0
125206 |  | AHUs shall be complete with suspension arrangement, it shall also include spring type vibration isolators and rubber groomets etc. to make the installation totally vibration free. AHUs shall have separate compartment for housing of all valves or extended insulated auxiliary drain tray. |  | 0.00 | 0.00 |  | 0
125207 |  | Multiblade box type zero leakage manually operated extruded aluminium volume control dampers shall be factory fitted at outlet of each AHU. |  | 0.00 | 0.00 |  | 0
125208 |  | In addition to the above, air handling units shall be provided with fire retardant flexible canvass connections made out of canvass sleeve. Sizes of air handling units shall not exceed as mentioned in the design drawings and air handling units shall conform to the design parameters mentioned in specifications. |  | 0.00 | 0.00 |  | 0
125209 |  | Suction side of the TFA unit should have flange for connecting duct from outside |  | 0.00 | 0.00 |  | 0
125210 |  | The Air Handling Units (AHUs) shall be of following duty parameters |  | 0.00 | 0.00 |  | 0
125211 |  | AHU No Capacity S.P Motor Rows of Area to |  | 0.00 | 0.00 |  | 0
125212 |  | (TR Cfm) (mmWG) Rating coil be fed |  | 0.00 | 0.00 |  | 0
125213 |  | (HP) |  | 0.00 | 0.00 |  | 0
125214 |  | CSAH-2 31 5000 35 BOH Area | Nos | 0.00 | 1.00 |  | 0
125215 |  | TUBE AXIAL FAN |  | 0.00 | 0.00 |  | 0
125216 |  | Supply,Installation,Testing and Commissioning of Tube Axial Fan of following as per the specifications |  | 0.00 | 0.00 |  | 0
125217 |  | Size Upto dia 500mm CFM 3000 CFM SP 20mm Suitable for clean air normal ventilation and smokespill application Normal Ventilation 100°C Motor Totally enclosed Class F or H , with a minimum IP55 protection are fitted as standard. Standard motor up to 2.2kW are supplied with DOL starting, motor 3.0kW and above are with star delta starting Inlet and outlet duct connection flanges to connect circular duct to TDC flanges Vibration isolator mounts for floor or ceiling mounted installations A drain coupling to be attached to the bottom of housing Construction Double flanged casing is produced in mild steel or galvanized steel. The impeller blades are of PPG, PAG, or Aluminium alloy Coatings Zinc rich primer and polyester powder coating or galvanized finish for all mild steel parts. |  | 0.00 | 0.00 |  | 0
125218 |  | M c No Capacity S.P Motor Area to |  | 0.00 | 0.00 |  | 0
125219 |  | (Cfm) (mmWG) Rating be fed |  | 0.00 | 0.00 |  | 0
125220 |  | (HP) |  | 0.00 | 0.00 |  | 0
125221 |  | AS-1 3000 20 Kitchen FA | Nos | 0.00 | 1.00 |  | 0
125222 |  | STARTER PANEL - SITC of starter panel DOL type. Panel must include the main MCB, phase indicating lamp, Over load relay under over voltage relay, SPP, Tripping lamp etc. Panel should complete in all respect with MS fabrciated powder coated body. Wall mounted arrangement to be provided with hook. Earhting arrangement must be availalble. Cable entry should be available on top bottom both side. starter panel should be complete with all installation testing.NO NC contact to be provided within the starter panel for tripping of AHU in case of fire. Intergration to be done with FAS panel |  | 0.00 | 0.00 |  | 0
125223 |  | 32 Amps ,TP MCB -- 1set |  | 0.00 | 0.00 |  | 0
125224 |  | (0-500) V digital Voltmeter with built in Selectorswitch -- 1set |  | 0.00 | 0.00 |  | 0
125225 |  | Digital Ammeter with built in selector switch- 1set |  | 0.00 | 0.00 |  | 0
125226 |  | Current Transformers - 1set |  | 0.00 | 0.00 |  | 0
125227 |  | LED type RYB phase indication lights- 1set |  | 0.00 | 0.00 |  | 0
125228 |  | LED type ON OFF indication lights -- 1set |  | 0.00 | 0.00 |  | 0
125229 |  | 3HP DOL starter with built-in single phasing |  | 0.00 | 0.00 |  | 0
125230 |  | preventor overload relay adjustable timer -- 1 set |  | 0.00 | 0.00 |  | 0
125231 |  | START-STOP Push Buttons -- 1 set |  | 0.00 | 0.00 |  | 0
125232 |  | Auto-Manual type selector switch to facilitate auto start of AHUs -- 1set |  | 0.00 | 0.00 |  | 0
125233 |  | Contactors, Potential Free Contacts, Control wiring and safety circuit as required with start-stop push buttons stay put or lockable type -1set | Nos | 0.00 | 5.00 |  | 0