## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
147251 | 1 | Light Point Wiring |  | 0.00 | 0.00 |  | 0
147252 |  | Providing ceiling light 2 X2 X2 nos 6A socket outletpoint wiring using 4mm2 stranded class 2 copper conductor ZHFR insulated wires laid in 1.60mm thick MS BSE conduits; installed surface to ceiling concealed in walls, within timber partitions complete as directed and as per the layout drgs. Conduits shall be cleated to the surface walls with HG gauge GI saddles and spacers as per engg practice. Rate to include all conduits and accessories, wires. modular type wiring accessories with flush mounting MS yellow zinc passivated switch socket boxes complete and civil works and making good. NOTE ALL LIGHT POINTS SHALL BE TERMINATED WITH 3 WAY 20A CONNECTORS WITH SUFFICIENT SLACK OF WIRES in GI FLEXIBLE CONDUITS ONLY | nos | 0.00 | 2.00 |  | 2800
147253 |  | Rate to include supply and installation of |  | 0.00 | 0.00 |  | 0
147254 | 1.2 | Primary light point with DB controlled | nos | 0.00 | 6.00 |  | 2950
147255 | 1.3 | Signage point directly DB controlled | nos | 0.00 | 2.00 |  | 3500
147256 | 1.8 | Control circuit wiring with 3 x 2.5mm2 wires for dimming | nos | 0.00 | 2.00 |  | 2600
147257 | 2 | Power point wiring for 16A, 3 pin socket outlets - for general power only |  | 0.00 | 0.00 |  | 0
147258 |  | Providing power point wiring to 16A socket outlets using 2 x 4.0mm2 + 1 x 2.5mm2 stranded class 2 copper conductor ZHFR insulated wires laid in 1.60mm thick MS BSE conduits; installed surface to ceiling concealed in walls, within timber partitions complete as directed and as per the layout drgs. Conduits shall be cleated to the surface walls with HG gauge GI saddles and spacers as per engg practice. Rate to include all conduits and accessories, wires. modular type wiring accessories with flush mounting MS yellow zinc passivated switch socket boxes complete and civil works and making good. | nos | 0.00 | 8.00 |  | 2200
147259 |  | GENERAL POWER SOCKET (4mm2 wiring) |  | 0.00 | 0.00 |  | 0
147260 | 2.1 | 3pin 16A switched socket outlet with indicator as first point in circuit | nos | 0.00 | 2.00 |  | 3600
147261 | 2.2 | 3pin 16A switched socket outlet with indicator looping point in circuit - max 3 sockets to be looped | nos | 0.00 | 6.00 |  | 2800
147262 |  | EQUIPMENT WIRING |  | 0.00 | 0.00 |  | 0
147263 |  | Input Power Wiring from Cafe Panel DBs, laid partly in ceiling trunking and partly in surface trunking or conduits in walls partition drops etc. Rate to include supply and installation of 1.60mm thick MS BSE conduits. Wires shall be 650V, stranded class 2 copper conductor ZHFR insulated wires to IS 8130 latest. Wires shall be ISI branded and BIS approved. All connections at DB and Panel end shall be provided with lugs and ferrules for identification of DB and circuit no. Wires shall be colour coded as per the phase. Rate to exclude S I of Trunking and Wiring Accessories which is covered separately. |  | 0.00 | 0.00 |  | 0
147264 | 2.4 | Wiring for 16A 20A 25A 1PH Power Point with 2x4mm2 +1x2.5mm2 wires | m | 0.00 | 350.00 |  | 280
147265 |  | WIRING ACCESSORIES FOR EQUIPMENT |  | 0.00 | 0.00 |  | 0
147266 |  | S I T C of the following wiring accessories complete with flush mounting boxes and connections and earth as directed and as per specifications. All respective civil works are included in the quoted rate |  | 0.00 | 0.00 |  | 0
147267 | 2.6 | 3pin 16A switched socket outlet with indicator | nos | 0.00 | 42.00 |  | 600
147268 | 2.7 | Industrial type 20A plastic plug socket with 20A SP MCB in surface or concelaed as single point in circuit | nos | 0.00 | 14.00 |  | 2600
147269 |  | TABLE SOCKET POWER WIRING ACCESSORIES |  | 0.00 | 0.00 |  | 0
147270 | 2.1 | Table socket power wiring with 3c x 2.5mm2 copper flexible ZHFR ZHFR cable in under floor raceways under floor conduits. (Note raceways and conduits measured separately) for RAW power. Flex Cable shall be ZHFR insulated, ZHFR outersheath. | m | 0.00 | 150.00 |  | 200
147271 |  | WIRING ACCESSORIES FOR ABOVE |  | 0.00 | 0.00 |  | 0
147272 | 2.11 | S I of 3pin,6A switch socket outlet for RAW power.Configuration shall be 2 nos for RAW power with 1no 16A switch with I no. of USB port shall be fixed on wall partition or as per the architect directed at site. All sockets shall be provided with surface mounting PVC or flush mounting MS concealed back box. Colour of SSO will be WHITE. Rate to consider with MS concealed back box and all the necessary hardware required. | sets | 0.00 | 4.00 |  | 900
147273 | 2.12 | 100x100x50mm GI Back box for Data voice TV outlets concealed inside the wall partitions including all civil works | nos | 0.00 | 10.00 |  | 220
147274 | 3 | MS BSE Conduits (for surface wiring only) |  | 0.00 | 0.00 |  | 0
147275 |  | S I of 1.60mm MS BSE conduits with all the accessories bolts,screw,coupler,jb,3 4ways,etc, installed surface on ceiling, walls, partitions etc complete as per the specifications |  | 0.00 | 0.00 |  | 0
147276 | 3.1 | 25mm dia 1.60mm thick MS BSE conduit | m | 0.00 | 50.00 |  | 220
147277 | 3.2 | 25mm dia GI flexible conduits complete with coupler at both ends with all hardware | m | 0.00 | 15.00 |  | 125
147278 |  | PANELS DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
147279 |  | S I T C of the following panels,DBs with all fuses switches, MCBs, ELCBs, busbars interconnections, earthing, angle iron frame work, etc complete as per the specifications and drgs. |  | 0.00 | 0.00 |  | 0
147280 |  | REFER SLD FOR DETAILS |  | 0.00 | 0.00 |  | 0
147281 | 1 | MAIN DB WITH ELR, CBCT SHUNT TRIP | nos | 0.00 | 1.00 |  | 75000
147282 |  | TOTAL FOR PANELS DISTRIBUTION BOARDS |  | 0.00 | 0.00 |  | 0
147283 |  | CABLES TERMINATION |  | 0.00 | 0.00 |  | 0
147284 | 1 | SI T C of 1100V grade, stranded copper aluminum conductor, XLPE insulated, inner sheathed, armoured and overall FRLS PVC sheathed, cable to IS 7098 Pt (I) latest; cable installed within raised access floors, cleated on walls, trays etc with AL clamps, as indicated on the drg and as directed by the Architects Consultant. Rate to exclude all excavation, ducts, trays etc - measured sep. Rate to include all clamps GI saddles and spacers, hardware, cable identification tags, etc as per specifications. |  | 0.00 | 0.00 |  | 0
147285 |  | REFER SLD CABLE SCHEDULE FOR DETAILS |  | 0.00 | 0.00 |  | 0
147286 |  | AL. ARMOURED XLPE CABLES |  | 0.00 | 0.00 |  | 0
147287 | 1.2 | 3.5c x 35mm2 A2XFY AL XLPE PVC cable | m | 0.00 | 25.00 |  | 350
147288 | 2 | Cable end terminations with Double Compression type cable glands and crimping type copper or aluminium lugs, connections, hardware and earth and shrouds covering the gland. Note the earth shall be provided in continuity for all the glands within a panel with 2.5mm2 wire and the cost for the same shall be included in the quoted rate. Aluminium cables will be provided with aluminium lugs; copper cables shall be provided with copper lugs. In case the busbar material and lug material are different Bi metallic washers shall be provided for the same. note that the lug dimension and bolt dimension shall be same and there shall not be any play between the two. Spring and plain washers shall be provided for each lug |  | 0.00 | 0.00 |  | 0
147289 |  | AL. ARMOURED XLPE CABLES |  | 0.00 | 0.00 |  | 0
147290 | 2.2 | 3.5c x 25mm2 A2XFY AL XLPE PVC cable | nos | 0.00 | 3.00 |  | 1200
147291 |  | TOTAL FOR CABLES TERMINATION |  | 0.00 | 0.00 |  | 0
147292 |  | EARTHING AND GROUNDING SYSTEMS |  | 0.00 | 0.00 |  | 0
147293 | 1 | S I of the following sizes of earthing conductors laid in ground cleated on wall ceiling etc complete with all joints welding brazing etc and all hardware as per specs. |  | 0.00 | 0.00 |  | 0
147294 |  | GI Earth Strips |  | 0.00 | 0.00 |  | 0
147295 | 2.4 | 8SWG GI wire | m | 0.00 | 10.00 |  | 465
147296 |  | TOTAL FOR EARTHING AND GROUNDING SYSTEMS |  | 0.00 | 0.00 |  | 0
147297 |  | MISCELLANEOUS ITEMS |  | 0.00 | 0.00 |  | 0
147298 | 2 | Providing the following safety equipments accessories of I.S. approved make. |  | 0.00 | 0.00 |  | 0
147299 | 2.2 | First aid boxes with all standard contents. | set | 0.00 | 1.00 |  | 1200
147300 | 2.3 | Shock treatment instruction charts in Local Language English in good quality frame glass cover. | nos | 0.00 | 1.00 |  | 2300
147301 | 2.4 | Providing the Floor SLD printed on A2 A3 size paper and sticked on high quality wooden frame with glass cover in the floor electrical room | nos | 0.00 | 1.00 |  | 1000
147302 | 2.5 | Providing the 16 amp socket for geasur | nos | 0.00 | 2.00 |  | 850
147303 | 5 | TV SYSTEM WIRING |  | 0.00 | 0.00 |  | 0
147304 | 5.1 | Providing and pulling co axial RG 11 armoured cable for SMATV system main run per floor including all end connections and terminations (Considering RG 11 cable will be provided by airport authority team upto the store outlet, further cabling will be in scope of contractor) | m | 0.00 | 0.00 |  | 210
147305 | 5.2 | Providing and pulling co axial armoured RG6 cable for taps offs to TV outlets in different areas | m | 0.00 | 100.00 |  | 373
147306 | 5.3 | Providing and fixing at approved locations the following Splitters Tapp offs for SMATV System |  | 0.00 | 0.00 |  | 0
147307 |  | 3 Ways Tap offs Splitters. | nos | 0.00 | 1.00 |  | 450
147308 | 5.4 | Providing and fixing Modular TV Outlet BNC type connector in concealed MS Box. | nos | 0.00 | 4.00 |  | 2600