## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
157973 |  | DISTRIBUTION BOARDS - Supply, erection, testing and commissioning of the following sheet steel clad wall recess mounting dust and vermin proof double door type distribution boards constructed from 16 SWG sheet steel IP 42 construction, finished with rust proof duly powder coated in approved shade with hinged gasketed door and housing the following complete with P.V.C. insulated copper busbars rated 200 amp with interconnections, neutral and earth bar assembly per phase, earthing terminals complete as approved by Architects. Note - All MCBs in distribuition board for power circuits shall be of C curve |  | 0.00 | 0.00 |  | 0
157974 |  | Type A |  | 0.00 | 0.00 |  | 0
157975 |  | 1-63 amp FP MCB with 3 single phase banks each comprising of 63A DP RCCB(100 mA) and 6 nos. 6 or 16 or 20 or 25 amps SP 10 kA MCB(Type C) with thermal magnetic protective releases out goings. | Set | 0.00 | 1.00 |  | 45000
157976 |  | Sub meter | Set | 0.00 | 1.00 |  | 21500
157977 |  | Supply, laying, testing and commissioning of following sizes of Al or Cu. conductor 1.1 kV grade, non armoured, XLPE insulated FRLS LT Cables or Control Cables including necessary cleats, clamps etc. 4C – 4.0 (Cu.) FRLS flexible cable | Mtrs | 0.00 | 30.00 |  | 450
157978 |  | Wiring for switch controlled Normal primary light points with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade wires (FRLS) in 25 mm 16SWG MS Heavy Duty PVC concealed or surface conduit including cost of cutting and filling chases for recessed conduiting and supports in case of Surface conduit including all bends , saddles , Junction boxes etc. including the cost of running 2.5 sq. mm PVC insulated copper conductor wire for loop earthing etc. and including providing circuit wiring with 1.5 sq mm PVC insulated stranded copper conductor 1100 volt grade FRLS wires and including the cost of providing and fixing a 6 amp 240 Volt grid plate mounted switch with moulded cover plate in GI box and complete as required ( Switch shall be as approved by the architect or Client) | Pt. | 0.00 | 18.00 |  | 2250
157979 |  | Wiring for secondary Switch controlled normal light points ( Looped from above point) with 1.5 sq. mm PVC insulated stranded copper conductor 1100 Volt grade FRLS wires in 25 mm dia 16SWG MS concealed or surface conduit including cost of cutting and filling chases for recessed conduiting and supports in case of Surface conduit including all bends , saddles , Junction boxes etc and including the cost of running 1.5 Sq mm PVC insulated copper conductor wire for loop earthing etc. complete as required. | Pt. | 0.00 | 6.00 |  | 1450
157980 |  | Wiring for primary switch board consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A switch with PVC insulated stranded copper conductor 1100 volt grade wires (FRLS), 1.5 sq FRLS copper wire mm in 25mm dia 16 SWG MS conduit in wall or Ceiling including cost of providing saddles etc as required for surface conduiting and or or cost of cutting and filling chases and including providing and fixing prewired switch board each consisting of 3 Nos. 5 pin 240 volt 6 amp single phase and neutral switch socket outlets with 3 Nos. 6A modular switch , safety shutters in a recessed or surface GI box including earthing of the 3rd pin with 1.5 sq mm 1100 volt grade PVC insulated stranded copper conductor wire complete as required. (Switch or Socket Shall be as per approved sample by Architect) | Pt. | 0.00 | 35.00 |  | 2250
157981 |  | Supply and fixing of following approved make modular type switch socket outlet with shutter and cover plate housed in factory fabricated 16SWG ISI marked G.I. box duly recessed in wall and complete internal connections with PVC connector, Point is including FRLSH MMS PVC conduit with 2x4 plus 1x2.5 Sqmm. wiring circuit. joints and all fixing arrangements in all respect as per satisfaction of Engineer-In-Charge. 10metre circuit included |  | 0.00 | 0.00 |  | 0
157982 |  | 3 x 5 amp socket plus 15amp x1 nos switch set | Pt. | 0.00 | 23.00 |  | 1550
157983 |  | 6 amp switch | Pt. | 0.00 | 25.00 |  | 790
157984 |  | 15 amp switch and socket | Pt. | 0.00 | 20.00 |  | 950
157985 |  | Supply and installation of flush mounted (Enhanced Category 6T 568 A or B) outlets with 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover or blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. Duplex outlet face plate with RJ-45 Jack with information outlet | Nos. | 0.00 | 36.00 |  | 1075
157986 |  | Supply,installtion testing and commisioning of Cat-6A UTP cables in existing Conduit complete as required for Telephone and Data System | Mtrs | 0.00 | 650.00 |  | 160
157987 |  | Supply , fixing and Laying 16 SWG MS conduits on surface or concealed complete with PVC junction boxes, cover plates, bends, saddles, base and other accessories all made in PVC with GI screws as required to complete the job. 25 mm dia 16 SWG MS conduit | Mtrs | 0.00 | 120.00 |  | 210