## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
177396 | 1 | PANELS, SWITCHGEARS DISTRIBUTION BOARD- HEAD -1 DETAILS |  | 0.00 | 0.00 |  | 0
177397 | 1.1 | MAIN PANEL-1 | Nos. | 0.00 | 0.00 |  | 0
177398 |  | Incomer 125 AMPS 4P MCCB, 36kA with TM Based O C SC Release. |  | 0.00 | 0.00 |  | 0
177399 |  | Meter Protection ELR with CBCT; 150 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  | 0.00 | 0.00 |  | 0
177400 |  | Indication Phase indicating lamps with 6A MCB |  | 0.00 | 0.00 |  | 0
177401 |  | Busbar 150A TPN Cu Busbar |  | 0.00 | 0.00 |  | 0
177402 |  | Outgoings |  | 0.00 | 0.00 |  | 0
177403 |  | a) 40A 4P MCCB, 16kA, TM BASED-1 Nos. |  | 0.00 | 0.00 |  | 0
177404 |  | b) 63A 4P MCB, 10kA, TM BASED-1 Nos. |  | 0.00 | 0.00 |  | 0
177405 |  | c) 40A 4P MCB, 10kA, TM BASED-5 Nos. |  | 0.00 | 0.00 |  | 0
177406 |  | d) 32A 4P MCB, 10kA, TM BASED-2 Nos. |  | 0.00 | 0.00 |  | 0
177407 |  | e) 16-32A 2P MCB, 10kA, TM BASED-25 Nos. |  | 0.00 | 0.00 |  | 0
177408 |  | f) 10A SP MCB, 10kA, TM BASED-02 Nos. |  | 0.00 | 0.00 |  | 0
177409 | 1.2 | MAIN PANEL-2 | Nos. | 0.00 | 0.00 |  | 0
177410 |  | Incomer 40 AMPS 4P MCCB, 25kA with TM Based O C SC Release. |  | 0.00 | 0.00 |  | 0
177411 |  | Meter Protection ELR with CBCT; 40 5A, 15VA, CL-1 CT s -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG) |  | 0.00 | 0.00 |  | 0
177412 |  | Indication Phase indicating lamps with 6A MCB |  | 0.00 | 0.00 |  | 0
177413 |  | Busbar 75A TPN Cu Busbar |  | 0.00 | 0.00 |  | 0
177414 |  | Outgoings |  | 0.00 | 0.00 |  | 0
177415 |  | a) 32A 4P MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
177416 |  | b) 25A 4P MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
177417 |  | c) 32A DP MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
177418 |  | d) 40A DP MCB, 10kA-1 Nos. |  | 0.00 | 0.00 |  | 0
177419 | 2 | SWITCHGEARS DISTRIBUTION BOARD |  | 0.00 | 0.00 |  | 0
177420 |  | Supplying installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards Switchgears. (IP-43) ACRY DB |  | 0.00 | 0.00 |  | 0
177421 |  | Provide insulated dedicated earth link for UPS DB |  | 0.00 | 0.00 |  | 0
177422 |  | All MCB s for UPS shall be D Curve, C Curve for Power B Curve for Lighting. |  | 0.00 | 0.00 |  | 0
177423 | 2.1 | SWITCHGEARS |  | 0.00 | 0.00 |  | 0
177424 |  | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears. | Nos. | 0.00 | 0.00 |  | 0
177425 |  | 63 40 32 20 amps 4P MCB C TYPE with complete with all mounting accessories – for Indoor Legrand make | Nos. | 0.00 | 0.00 |  | 0
177426 |  | 63 40 32 20 amps DP MCB C TYPE with complete with all mounting accessories – IP-65 | Nos. | 0.00 | 0.00 |  | 0
177427 |  | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 0.00 |  | 0
177428 |  | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 0.00 |  | 0
177429 |  | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 0.00 |  | 0
177430 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 0.00 |  | 0
177431 | 2.2 | DISTRIBUTION BOARDS- HEAD -2 DETAILS |  | 0.00 | 0.00 |  | 0
177432 |  | 6 WAY SPN DB - UPS DB | Nos. | 0.00 | 1.00 |  | 0
177433 |  | Incomer 20 AMPS DP MCB 10KA 1 Nos. |  | 0.00 | 0.00 |  | 0
177434 |  | Outgoings 6 10 16 A SP MCB B Type - 4 Nos. |  | 0.00 | 0.00 |  | 0
177435 |  | 8 WAY TPN PPI DB - Light, Power | Nos. | 0.00 | 2.00 |  | 0
177436 |  | Incomer 63A, FP, MCB, 10kA 1 Nos |  | 0.00 | 0.00 |  | 0
177437 |  | Sub Incomer 40A, DP, RCBO, 100mA 3 Nos |  | 0.00 | 0.00 |  | 0
177438 |  | Outgoings 10 16 20 25 A SP MCB C Type - 24 Nos. |  | 0.00 | 0.00 |  | 0
177439 |  | 12 WAY VTPN DB - POWER POINT | Nos. | 0.00 | 1.00 |  | 0
177440 |  | Incomer 64 AMPS FP RCBO 100mA |  | 0.00 | 0.00 |  | 0
177441 |  | Outgoings 10 32 64 A FP MCB C Type - 10 Nos. |  | 0.00 | 0.00 |  | 0
177442 | 2 | MV CABLES |  | 0.00 | 0.00 |  | 0
177443 | 2.1 | POWER CABLING |  | 0.00 | 0.00 |  | 0
177444 |  | Supply and laying, effecting proper connections, testing commissioning of the following sizes of 1.1 KV XLPE FRLS armoured unarmoured PVC insulated PVC sheathed aluminium copper conductor cables conforming to IS 1554 and IS 694 for Flexible copp |  | 0.00 | 0.00 |  | 0
177445 |  | Aluminium cables |  | 0.00 | 0.00 |  | 0
177446 |  | 3.5C x 70 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177447 |  | 3.5C x 50 Sq.mm. | Mtr. | 0.00 | 50.00 | 0.00 | 0
177448 |  | 4C x 16 Sq.mm. | Mtr. | 0.00 | 10.00 | 0.00 | 0
177449 |  | 4C x 10 Sq.mm. | Mtr. | 0.00 | 50.00 | 0.00 | 0
177450 |  | 4C x 6 Sq.mm. | Mtr. | 0.00 | 50.00 | 0.00 | 0
177451 |  | - do - but for copper cables |  | 0.00 | 0.00 |  | 0
177452 |  | 4C x 25 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177453 |  | 4C x 16 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177454 |  | 4C x 10 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177455 |  | 4C x 6 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177456 |  | 4C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177457 |  | 4C x 2.5 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177458 |  | 3C x 6 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177459 |  | 3C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177460 |  | 3C x 2.5 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177461 |  | CU Flexible Cables |  | 0.00 | 0.00 |  | 0
177462 |  | 4C x 6 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177463 |  | 4C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177464 |  | 3C x 4 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177465 |  | 3C x 2.5 Sq.mm. | Mtr. | 0.00 | 0.00 | 0.00 | 0
177466 |  | 2C x 2.5 Sq.mm. for Earthing | Mtr. | 0.00 | 0.00 | 0.00 | 0
177467 |  | , - do - but for copper flexible cables |  | 0.00 | 0.00 |  | 0
177468 |  | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | Mtr. | 0.00 | 0.00 | 0.00 | 0
177469 |  | TOTAL FOR POWER CABLES |  | 0.00 | 0.00 | 0.00 | 0
177470 | 2.2 | CABLE TERMINATION |  | 0.00 | 0.00 |  | 0
177471 |  | Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  | 0.00 | 0.00 |  | 0
177472 |  | 3.5C x 70 Sq.mm. AL | Nos. | 0.00 | 0.00 | 0.00 | 0
177473 |  | 3.5C x 50 Sq.mm. AL | Nos. | 0.00 | 1.00 | 0.00 | 0
177474 |  | 4C x 16 Sq.mm. AL | Nos. | 0.00 | 2.00 | 0.00 | 0
177475 |  | 4C x 10 Sq.mm. AL | Nos. | 0.00 | 4.00 | 0.00 | 0
177476 |  | 4C x 6 Sq.mm. AL | Nos. | 0.00 | 1.00 | 0.00 | 0
177477 |  | 4C x 6 Sq.mm. CU | Nos. | 0.00 | 0.00 | 0.00 | 0
177478 |  | 4C x 4 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177479 |  | 4C x 2.5 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177480 |  | 3C x 6 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177481 |  | 3C x 4 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177482 |  | 3C x 2.5 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177483 |  | Flexible cable |  | 0.00 | 0.00 |  | 0
177484 |  | 4C x 6 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177485 |  | 4C x 4 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177486 |  | 3C x 4 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177487 |  | 3C x 2.5 Sq.mm. (Lighting) | Nos. | 0.00 | 0.00 | 0.00 | 0
177488 |  | 2C x 2.5 Sq.mm. | Nos. | 0.00 | 0.00 | 0.00 | 0
177489 | 3 | RACEWAYS AND CABLE TRAYS HEAD-3 DETAILS |  | 0.00 | 0.00 |  | 0
177490 | 3.1 | TRUNKING Fabricating supplying to site of installation, installation on ceiling surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and |  | 0.00 | 0.00 |  | 0
177491 |  | 100 mm (wide) x 100 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177492 |  | 50 mm (wide) x 50 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177493 | 3.2 | RACEWAY Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 m |  | 0.00 | 0.00 |  | 0
177494 |  | 100 mm (wide) x 40 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177495 |  | 65 mm (wide) x 40 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177496 | 3.3 | JUNCTION BOXES Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated fla |  | 0.00 | 0.00 |  | 0
177497 |  | (variation in height may be considered for quoting as floor thickness may vary) |  | 0.00 | 0.00 |  | 0
177498 |  | 250 mm x 250 x 60 50 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177499 |  | 150 mm x 150 x 60 50 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177500 |  | 100 mm x 150 x 60 50 mm (height) | Mtr. | 0.00 | 0.00 |  | 0
177501 | 3.4 | CABLE TRAY Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured unarmoured aluminium copper conductor cables. Fabricate the cable trays from perforated 1.6 2mm thick M.S. CRCA she |  | 0.00 | 0.00 |  | 0
177502 |  | 300 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 0.00 |  | 0
177503 |  | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 30.00 |  | 0
177504 |  | 100 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 0.00 |  | 0
177505 |  | 50 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0.00 | 0.00 |  | 0
177506 | 4 | POINT WIRING-HEAD -4 DETAILS |  | 0.00 | 0.00 |  | 0
177507 |  | Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. |  | 0.00 | 0.00 |  | 0
177508 |  | The secondary Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. |  | 0.00 | 0.00 |  | 0
177509 |  | All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. |  | 0.00 | 0.00 |  | 0
177510 |  | The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  | 0.00 | 0.00 |  | 0
177511 |  | The Length shall be paid as per the actual measurements as per following manner. |  | 0.00 | 0.00 |  | 0
177512 | 4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in PVC FRLS conduits in F.ceiling walls ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switch |  | 0.00 | 0.00 |  | 0
177513 |  | From DB to Normal Switch Board | Nos. | 0.00 | 0.00 |  | 0
177514 |  | From DB to Emergency Switch Board | Nos. | 0.00 | 0.00 |  | 0
177515 | 4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in PVC FRLS conduits in F.ceiling walls ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc |  | 0.00 | 0.00 |  | 0
177516 |  | First point controlled by one no. 6amp MCB. (upto 25Mtr.) | Nos. | 0.00 | 10.00 |  | 0
177517 |  | First point controlled by one no. 6 amp MCB. (upto 30Mtr.) | Nos. | 0.00 | 6.00 |  | 0
177518 |  | First point controlled by one no. 6 amp MCB. For Emergency Light (upto 10Mtr.) | Nos. | 0.00 | 4.00 |  | 0
177519 |  | First point controlled by one no. 6 amp MCB. For Emergency Light (upto 20Mtr.) | Nos. | 0.00 | 2.00 |  | 0
177520 | 4.3 | Same as item No. 4.2.1 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed PVC FRLS conduit and earthing | Nos. | 0.00 | 0.00 |  | 0
177521 | 4.4 | Same as item No. 4.2.3 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed exposed PVC FRLS conduit and earthing For Emergency Light | Nos. | 0.00 | 0.00 |  | 0
177522 | 4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed exposed PVC FRLS conduits as called for and earthing. |  | 0.00 | 0.00 |  | 0
177523 |  | First point controlled by existing MCB in D.B. (upto 25Mtr.) | Nos. | 0.00 | 23.00 |  | 0
177524 |  | First Emergency point controlled by existing MCB in D.B. (upto 25Mtr.) | Nos. | 0.00 | 21.00 |  | 0
177525 | 4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed PVC FRLS conduit and earthing (upto 25Mtr.) | Nos. | 0.00 | 30.00 |  | 0
177526 | 4.7 | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed exposed M.S. conduit and earthing For Emergency Lighting (upto 25Mtr.) | Nos. | 0.00 | 20.00 |  | 0
177527 | 4.8 | Wiring for UPS Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 0.00 | 375.00 |  | 0
177528 | 4.9 | Wiring for UPS Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS 694-1990 with latest amendments, in existing Channels con | Mtr. | 0.00 | 300.00 |  | 0
177529 | 4.1 | Providing and fixing in position the following PVC FRLS conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the leng |  | 0.00 | 0.00 |  | 0
177530 |  | 20 mm dia PVC FRLS Conduit | Mtr. | 0.00 | 500.00 |  | 0
177531 |  | 25 mm dia PVC FRLS Conduit | Mtr. | 0.00 | 75.00 |  | 0
177532 | 4.11 | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling wall floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the l |  | 0.00 | 0.00 |  | 0
177533 |  | 20 mm dia PVC FRLS Conduit | Mtr. | 0.00 | 100.00 |  | 0
177534 |  | 25 mm dia PVC FRLS Conduit | Mtr. | 0.00 | 20.00 |  | 0
177535 | 4.12 | Supply Laying of DATA CABLE CAT 6 in 20mm dia. PVC FRLS Conduit for DATA | Mtr. | 0.00 | 180.00 |  | 0
177536 | 5 | MODULAR SWITCHES-HEAD5 DEATILS |  | 0.00 | 0.00 |  | 0
177537 | 5.1 | Supply, installation, testing commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB n |  | 0.00 | 0.00 |  | 0
177538 |  | 6A One Way Switch | Nos. | 0.00 | 10.00 |  | 0
177539 |  | 6A 5 pin Socket - 1Nos. 6A Switch - 1Nos. | Nos. | 0.00 | 5.00 |  | 0
177540 |  | 6 16A Socket outlet - 1Nos. 16A Switch - 1Nos.(Raw UPS Power) | Nos. | 0.00 | 21.00 |  | 0
177541 |  | 5 15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0.00 | 11.00 |  | 0
177542 |  | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 0.00 | 6.00 |  | 0
177543 |  | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 0.00 | 3.00 |  | 0
177544 |  | 20 Amp 1- Ph Electrical Outlet | Nos. | 0.00 | 2.00 |  | 0
177545 |  | Data Outlet (RJ-45) | Nos. | 0.00 | 2.00 |  | 0
177546 |  | Telephone Outlet (RJ-11) | Nos. | 0.00 | 0.00 |  | 0
177547 | 6 | GENERAL EARTHING-HEAD -6 DETAILS |  | 0.00 | 0.00 |  | 0
177548 | 6.1 | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall Cable trays Hume pipes etc. The jointes shall be Bolted Welded. The joints shall be painted with bituminous paint in an approved manner. |  | 0.00 | 0.00 |  | 0
177549 |  | 25 x 3 mm | Mtr. | 0.00 | 0.00 |  | 0
177550 | 6.2 | Supplying and erecting bare GI conductor of following sizes |  | 0.00 | 0.00 |  | 0
177551 |  | 8 SWG | Mtr. | 0.00 | 50.00 |  | 0
177552 | 7 | LIGHT FIXTURES INSTALLATION-HEAD -7 DETAILS |  | 0.00 | 0.00 |  | 0
177553 | 7.1 | Receiving from Store, Installation, testing commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook Rods as per final approval from Architect Client Consultant |  | 0.00 | 0.00 |  | 0
177554 |  | ROUND CEILING LIGHT-01 | Nos. | 0.00 | 10.00 |  | 0
177555 |  | ROUND CEILING LIGHT-02 | Nos. | 0.00 | 53.00 |  | 0
177556 |  | ROUND CEILING LIGHT-03 | Nos. | 0.00 | 34.00 |  | 0
177557 |  | ROUND CEILING LIGHT-04 | Nos. | 0.00 | 11.00 |  | 0
177558 |  | PENDANT LIGHT-01 | Nos. | 0.00 | 4.00 |  | 0
177559 |  | PENDANT LIGHT-02 | Nos. | 0.00 | 2.00 |  | 0
177560 |  | PENDANT LIGHT-03 | Nos. | 0.00 | 1.00 |  | 0
177561 |  | PENDANT LIGHT-04 | Nos. | 0.00 | 6.00 |  | 0
177562 |  | WALL LIGHT | Nos. | 0.00 | 6.00 |  | 0
177563 |  | COVE LIGHT | Mtr. | 0.00 | 10.00 |  | 0
177564 | 9 | FAS System HEAD -9 DETAILS |  | 0.00 | 0.00 |  | 0
177565 | 9.1 | SITC of conventional type Manual call point complete with Glass, hammer and chain etc. as required. | Nos. | 0.00 | 1.00 |  | 0
177566 | 9.2 | SITC of conventional type Smoke Detector complete. as required. | Nos. | 0.00 | 24.00 |  | 0
177567 | 9.3 | SITC of conventional type Heat Detector complete. as required. | Nos. | 0.00 | 3.00 |  | 0
177568 | 9.4 | SITC of electronic hooters with LMT (hooters shall also be able to work as public address system sounders) housed in sheet steel Polymer housing suitable for wall ceiling and surface recess mounting including making connections with wires complete i | Nos. | 0.00 | 2.00 |  | 0
177569 | 9.5 | SITC of wall floor type following zone (each zone accessing minimum 20 units (detectors devices ) Conventional Type microprocessor based with LCD display main control panel fabricated from 16 SWG CRCA sheet steel sealed maintenance free (SMF) batterie |  | 0.00 | 0.00 |  | 0
177570 | 9.6 | 2 zone | Nos. | 0.00 | 1.00 |  | 0
177571 | 9.7 | SITC of conventional type microprocessor based Remote Annunciator panel of following zones for wall mounting type fabricated out of 16 SWG CRCA sheet steel incorporating audio visual indication for each zone without battery bank and battery charger . | Nos. | 0.00 | 1.00 |  | 0
177572 | 9.8 | Supply and drawing FRLS Fire Alarm Cable As Per IS . |  | 0.00 | 0.00 |  | 0
177573 | 9.9 | 2 x 1.5 sq mm | Mtr | 0.00 | 500.00 |  | 0
177574 | 10 | UPS System -HEAD- 10 DETAILS |  | 0.00 | 0.00 |  | 0
177575 | 10.1 | Supply,Installation, testing and commissioning of following type of Online UPS Inverter as per drawings and specifications with all other accessories. | Nos. | 0.00 | 1.00 |  | 0
177576 |  | Online UPS |  | 0.00 | 0.00 |  | 0
177577 |  | 3.0KVA UPS |  | 0.00 | 0.00 |  | 0
177578 |  | 12V DC 25AH maintenance free batteries for 30 minutes battery backup. |  | 0.00 | 0.00 |  | 0
177579 |  | Input supply voltage -230-250 Volts |  | 0.00 | 0.00 |  | 0
177580 |  | Output voltage -220-240V+ -1% |  | 0.00 | 0.00 |  | 0
177581 |  | Voltage Regulation -Less than or equal to + - 1% |  | 0.00 | 0.00 |  | 0
177582 |  | Output frequency -50 Hz + - 0.05 Hz |  | 0.00 | 0.00 |  | 0
177583 |  | Type of cooling -Forced air cooled |  | 0.00 | 0.00 |  | 0
177584 |  | Invertor Efficiency -Better than 85% |  | 0.00 | 0.00 |  | 0
177585 |  | Output Power factor -0.8 |  | 0.00 | 0.00 |  | 0
177586 | 11 | CCTV CABLE LAYING-HEAD- 11 DETAILS |  | 0.00 | 0.00 |  | 0
177587 |  | Supply, Drawing and Testing of 4+1 cable as per latest specifications for CCTV points in PVC FRLS conduits including making connections to Information outlets and patch panels with ferruling at both ends for identification with necessary tools for punching ,stripping crimping and testing as required included with RJ45 & IO as per the requirement. | Mtrs | 0.00 | 600.00 |  | 0
177588 | 12 | LIST OF APPROVED MAKES FOR ELECTRICAL EQUIPMENT MATERIALS HEAD-12 |  | 0.00 | 0.00 |  | 0
177589 |  | Equipment materials | Makes | 0.00 | 0.00 |  | 0
177590 | 1 | Low voltage switchgear enclosure (415v) (iec 61439 compliant) switchgears | Schneider legrand siemens abb l&t | 0.00 | 0.00 |  | 0
177591 | 2 | Ups system (uninterruptable power supply) (415 230v) | Apc-schneider eaton socomec vertiv | 0.00 | 0.00 |  | 0
177592 | 3 | Vrla smf battery | Excide amararaja rocket | 0.00 | 0.00 |  | 0
177593 | 4 | Dbs | Legrand - ekinoxe schneider - acti9 siemens abb | 0.00 | 0.00 |  | 0
177594 | 5 | Vfd (variable frequency drive) | Allen bradley alstom danfoss siemens abb l&t yaskawa honeywell | 0.00 | 0.00 |  | 0
177595 | 6 | Motor starter | Abb schneider siemens l&t | 0.00 | 0.00 |  | 0
177596 | 7 | Cable (415v) | Rpg finolex universal havells | 0.00 | 0.00 |  | 0
177597 | 8 | Disconnect switch | Schneider abb siemens l&t | 0.00 | 0.00 |  | 0
177598 | 9 | Wires copper flexible cable | Finolex havells rajnigandha rr kabel | 0.00 | 0.00 |  | 0
177599 | 10 | Raceways and junction boxes | Mk legrand obo bettermann | 0.00 | 0.00 |  | 0
177600 | 11 | Cable trays | Obo bettermann legrand indiana profab | 0.00 | 0.00 |  | 0
177601 | 12 | Spd (surge arraster) | Obo legrand schneider | 0.00 | 0.00 |  | 0
177602 | 13 | Meters (analog) | Meco rishabh nippen conserve ae | 0.00 | 0.00 |  | 0
177603 | 14 | Meters (digital) | Ae schneider nippen conserve l&t | 0.00 | 0.00 |  | 0
177604 | 15 | Energy meter , load manager | Schneider (em 6400ng or equivalent) l&t nippen hpl socomec | 0.00 | 0.00 |  | 0
177605 | 16 | Indicating lamps | Schneider l & t salzer | 0.00 | 0.00 |  | 0
177606 | 17 | Rotary switch | Siemens keycee salzer meco | 0.00 | 0.00 |  | 0
177607 | 18 | Push button and push button set | Siemens schneider electric l & t legrand c&s abb | 0.00 | 0.00 |  | 0
177608 | 19 | Selector switch | Keycee salzer meco | 0.00 | 0.00 |  | 0
177609 | 20 | Gi conduits and accessories | Bharat supreme bec | 0.00 | 0.00 |  | 0
177610 | 21 | Control transformer [ pt ct ] | Ashmor kappa elmex | 0.00 | 0.00 |  | 0
177611 | 22 | Fire barrier | Obo bettermann hilti 3m | 0.00 | 0.00 |  | 0
177612 | 23 | Terminal block | Essen connect well elmex | 0.00 | 0.00 |  | 0
177613 | 24 | Control switch | Alstom kaycee switron | 0.00 | 0.00 |  | 0
177614 | 25 | Hrc fuse | Siemens l&t alstom s&s cgl ge standard | 0.00 | 0.00 |  | 0
177615 | 26 | Limit switch | Siemens essen bch ind syndicate epcc(kakku) | 0.00 | 0.00 |  | 0
177616 | 27 | Elr with cbct | Kalpa jvc prok dv’s | 0.00 | 0.00 |  | 0
177617 | 28 | Overload relays with built in single phase preventer | Siemens abb l&t schneider | 0.00 | 0.00 |  | 0
177618 | 29 | Power aux. Contactor | L&t schneider | 0.00 | 0.00 |  | 0
177619 | 30 | Auxiliary relays | Siemens ge alstom abb jvs prok dv’s | 0.00 | 0.00 |  | 0
177620 | 31 | Protection relay - electromagnetic type | Areva | 0.00 | 0.00 |  | 0
177621 | 32 | Protection relay - numeric type | Areva siemens l&t sel | 0.00 | 0.00 |  | 0
177622 | 33 | 1.1kv, grade lt fire survival cables | Anchor finolex havells kei kec | 0.00 | 0.00 |  | 0
177623 | 34 | Signal cable | Enercon lapp india system tek caliplast eminent | 0.00 | 0.00 |  | 0
177624 | 35 | Cable lugs | Dowell’s 3d hex jainson comet hmi | 0.00 | 0.00 |  | 0
177625 | 36 | Bimetallic lugs | Hmi hex connect | 0.00 | 0.00 |  | 0
177626 | 37 | Cable glands | 3d comet hmi | 0.00 | 0.00 |  | 0
177627 | 38 | Lt cable jointing kits(cold curing) | Reychem 3m | 0.00 | 0.00 |  | 0
177628 | 39 | Pvc tape | Steel grip isi apprved | 0.00 | 0.00 |  | 0
177629 | 40 | Pvc junction box | Hensel clipsal spelsberg scame sintex | 0.00 | 0.00 |  | 0
177630 | 41 | Ceiling fan exhaust fan | Crompton bajaj orient havells | 0.00 | 0.00 |  | 0
177631 | 42 | Electric timer | Siemens legrand l&t meco telemechanique | 0.00 | 0.00 |  | 0
177632 | 43 | Connectors (colours as per phase neutral) | Wago phoenix contact connectwell | 0.00 | 0.00 |  | 0
177633 | 44 | Industrial socket with mcb | Legrand schneider mennekes | 0.00 | 0.00 |  | 0
177634 | 45 | Modular switches, sockets other accessories | Mk – blenze legrand-arteor schnedier-zencelo norisys l&t anchor - woods hpl - smart c&s-primo havells - crabtree | 0.00 | 0.00 |  | 0
177635 | 46 | Metal clad socket with mcb | Legrand hensel schneider scame spelsberg | 0.00 | 0.00 |  | 0
177636 | 47 | Public spaces light fixtures | Philips lighting technology regent zumtobel jaquar iguzzini erco endo bega lumenpulse or As per final approval of fixture by architects. | 0.00 | 0.00 |  | 0
177637 | 48 | Insulating mat | Jyoti premier polyfilm limited (electromat) | 0.00 | 0.00 |  | 0
177638 | 49 | Eathing material | Obo jef cape | 0.00 | 0.00 |  | 0