## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
127298 |  | 8.0TR - (3200CFM) - Supply Installation ,Supply, installation testing commissioning of Double skin construction draw thru type AIR HANDELING UNIT. Direct Driven Backward Curved Plug Fans with VFD, with Squirrel cage IE2 induction motor, GSS frame supporting frame work, Plug type fan, vibration isolators, base frame, Motor shall be suitable for operation of Variable Frequency Drive operation with 415±10% volts, 3 phase AC supply.cost included for VFD. Coils shall have 12.5 to 15 mm dia (O.D )tubes minimum 0.35 mm thick with sine wave aluminium fins firmly bonded to copper tubes assembled in zinc coated steel frame. Face and surface areas shall be such as to ensure rated capacity from each unit and such that the air velocity across the coil shall not exceed 150 meters per minute. The coil shall be pitched in the unit casing for proper drainage. The coil shall have suitable size header with DX COIL supply return connections protruding out of AHU casing by minimum 150 mm. Each coil shall be factory-tested at 21 kg per sq. m air pressure under water. Tube shall be mechanically expanded for minimum thermal contact resistance with fins. Fin spacing shall be 8 - 12 fins per cm. Water pressure drop in coil shall not exceed 10 PSIG. (Including THERMOSTAT WITH REMOTE CONTROL cable) | NOS | 0.00 | 2.00 |  | 0
127299 |  | 50 mm dia ,Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 6.00 |  | 0
127300 |  | 40 mm dia,Supply, delivery, installation, testing of MS C class piping complete with fittings (bends, Tees, reducers, flanges etc.)of class O elastomeric 13mm Nitrile Rubber with 2 coats – one on the insulated surface along with Glass Cloth | Rmt | 0.00 | 10.00 |  | 0
127301 |  | 50 mm dia - Butterfly Valves with steel shaft and cast iron body (PN 10) Supply, delivery, Installation testing of Valves with insulation as per specifications.,Approved Make - Zoloto | Nos | 0.00 | 2.00 |  | 0
127302 |  | 40 mm dia - Butterfly Valves with steel shaft and cast iron body (PN 10) Supply, delivery, Installation testing of Valves with insulation as per specifications.,Approved Make - Zoloto | Nos | 0.00 | 4.00 |  | 0
127303 |  | 40 mm dia - Y Strainers with cast iron fabricated steel body (PN 10) | Nos | 0.00 | 2.00 |  | 0
127304 |  | 40 mm dia - 2 way Control valve Supply, installation, testing and commissioning of complete set of control valve kit comprising of Two Way Control Valve of C.I body of PN16 ratings, motorized modulating actuators with linear stroke of minimum 15 mm, AHU room,one thermowell,one power supply unit of 230Vac 24Vac.Tranparent IP55 Control box for mounting Digital controller and power supply unit.The valve size shall be suitable for pipe size coil capacity | Nos | 0.00 | 4.00 |  | 0
127305 |  | Auto Air Vents with ball valve - 25 mm dia. | Nos | 0.00 | 4.00 |  | 0
127306 |  | Purge valve - 25 mm dia. | Nos | 0.00 | 4.00 |  | 0
127307 |  | Pressure gauges as per specification for mounting on chilled water pipe (Range 0 - 10 kg cm2) with cock and U pipe with ball valve. - Pressure Gauges | Nos | 0.00 | 4.00 |  | 0
127308 |  | Temperature gauges as per specification for mounting on pipe. (Range 0 - 50°C) with brass thermowells for mounting temperature gauges on chilled water line. - Temperature Gauges | Nos | 0.00 | 4.00 |  | 0
127309 |  | 32 mm - Drain pipe , drain pipe PVC complete with fitting, U trap, Support, receiving funnel preformed 3mm insulation. | Rmt | 0.00 | 15.00 |  | 0
127310 |  | 0.63 mm (24 SWG) GSS ducting (601mm-750mm) Supply, fabrication, installation and testing of GSS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for GS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. Ducts to be fabricated at the jobsite. factory Fabrication work shall be limited to assembly, installation and suit to site pieces and collars droppers The quoted costs should include i) Ducts with reinforcement strengthening ii) Air tight joints iii) Accessories such as splitter, damper, guide vane etc. iv) Hangers and supports (Gripple Supporting method to be used wherever required) v) Painting with Black color paint for duct sides behind the grills. vi) The gasket used in case for all ducts shall be fire retardant type vii) Ducts shall be fully sealed with Silicon Sealant for leak tight installation. Ducts shall be leak pressure tested leakages should be within acceptable limits as specified at Min. 500 Pa | Sqmt | 0.00 | 35.00 |  | 0
127311 |  | 13 mm thick - Insulation of Duct, Supplying and fixing of following thickness under deck Nitrie Rubber ( Class O type of fire retadancy). (Make - Hira Technologies) | Sqmt | 0.00 | 40.00 |  | 0
127312 |  | 1.09 mm (18 MSG) MS ducting (PLENUM),- Rectangular Ducting in Galvanised Steel Supply, fabrication, installation and testing of MS SS metal ducts as per IS-277 (120 GSM both sides, LFQ confirming to Class VIII) for MS SS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. | Sqm | 0.00 | 12.00 |  | 0
127313 |  | 13 mm thick - I,nsulation of Duct ,Supplying and fixing of following thickness duly laminated aluminum foil of mat finish. (Make - Hira Technologies) | Sqmt | 0.00 | 15.00 |  | 0
127314 |  | Supply, installation and testing of GI construction louver dampers within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system VOLUME CONTROL DAMPER IN DUCTING | Sqm | 0.00 | 1.50 |  | 0
127315 |  | Supplying fixing of black mat finish extruded aluminum opposed blade BLACK volume control dampers in supply air duct collars as per approved shop drawings and specifications VOLUME CONTROL DAMPER IN DUCTING | Nos | 0.00 | 4.00 |  | 0
127316 |  | 450 x 150mm - Extruded Aluminum Powder Coated Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as following sizes. | Nos. | 0.00 | 18.00 |  | 0
127317 |  | 150mm Width , Extruded Aluminum Powder Coated Continuous Linear Grilles Of Required Airflow Angles Without V.C.D- EP -00 15 30 with four side flanges as per requirements. | Rmt | 0.00 | 12.00 |  | 0