## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
149012 | A | SPLIT UNITS Supply , Installation, Testing and Commissioning of split units, each comprising of an outdoor and a single indoor unit as shown on the drawings and as per the specifications. Enclosures shall be factory fabricated and painted to a smooth finish. Oudoor unit shall consist of hermatically sealed semi- hermatic scroll rotary compressor s, air cooled condenser with fan. Indoor unit shall consist of fan section with dynamically balanced centrifugal fan s driven by FHP TEFC squirrel cage induction motor, multirows deep DX- copper cooling coil with aluminium fins, thermostatic expansion valve, synthetic fibre filters, insulated drain pan, safety controls, safety controls, thermostat all complete in a unit. The quoted price shall be inclusive of full charge of refrigerant gas, vibration isolation arrangement. Refrigerant Shall be R-32 R410A R407C Three phase ductable split units with Scroll compressor Unit should be suitable to handle total 35-40RM inter unit referigerant piping inlcuding 12-15RM vertical length. 8.5TR nominal capacity, split unit with single ductable type indoor unit and factory fitted electrical arrangement corded remote. | No | 0.00 | 1.00 |  | 0
149013 | B | Single phase Non-ductable split units with Rotary compressor (Three Star Rating) (Units should be suitable to handle piping length upto 24-25 RM) 1.5TR nominal capacity, split unit with single Wall Mounted type indoor unit and cordless control . Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. | No | 0.00 | 2.00 |  | 0
149014 |  | SECTION B KITCHEN VENTILATION SYSTEM |  | 0.00 | 0.00 |  | 0
149015 |  | DOUBLE SKIN AIR COOLING MACHINES - With Fresh Air Intake Section (AIR WASHERS) Supply , Installation, Testing and Commissioning of double skin type evaporative air cooling machines (packaged type) each comprising of following as per the specifications Casing of air washer shall be in double skin construction. Inner skin shall be constructed out of24 gauge plain GS sheet outer skin in 24 gauge pre-plasticized GS sheet sandwitched between 50mm thick injected PU foam insulation of density not less than 40 Kg CuM and complete with marine light,limit switch inspection doors including control wiringas required. Air washer shall have access for all parts. Fan section complete with backward curved DIDW type centrifugal fan s, EFF1, IE3, IP-55, rated TEFC squirrel cageinduction motor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Centrifugal fans shall be coated with epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS).All fans should be AMCA certified. AirWasher shall be provided with Intake Section withF A openings as per approved shop drawing. Air washer wet section shall be complete with 300mm thick cellulose based paper fills, drift eliminators,water distribution system complete with FRP spray headers, strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow drainconnections, GI medium class piping and 3 1 phasemonobloc pumps of 1HP 1.5HP 2HP motor rating as required according to the capacity of air cooling machines. Inner skin of wet section including fills mounting frame shall be constructed out of stainless steel SS- 304 A grade of appropriate thickness .Sump shall be made out of 1.25mm thick SS-304 A grade stainless steel .Velocity across the paper fills not to exceed 500 FPM. Filter section complete with 50mm thick aluminiumwire mesh viscous metallic filters. Velocity across the filters shall not exceed 500 FPM. Airwasher should be provided with adequate space between eliminator fan to avoid water carryover.The Evaporative Air Cooling Machines (EAC) shall be of following duty parameters M c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)EAC-1 1x22500 58-60 1x15.0 Kitchen | No | 0.00 | 1.00 |  | 0
149016 | 1.2 | SCRUBBER (For Kitchen Exhaust) WET TYPE SCRUBBER Supply , Installation , Testing and Commissioning of wet type scrubber (packaged type) comprising of following as per the specifications Fan section complete with backward curved DIDW type centrifugal fan s, TEFC squirrel cage inductionmotor suitable to operate on 415+10%V, 50Hz,3 phase AC power supply and belt drive package.Casing of wet type scrubber shall be constructedout of 16 gauge GS sheet complete with inspectiondoors as required. Centrifugal fans shall be coatedwith epoxy paint as specified. Fan outlet velocity shall not be more than 2000 FPM (10.16 MPS). Wet section complete with double bank spray header in GI construction and nozzles, louvers PVC mist eliminators mist collection tray made out of 16G GSS,strainer of fine mesh brass screen, globe valve,float valve, quick fill, over flow drainconnections, GI medium class piping and 3 phasemonobloc pump of 1.5HP motor rating as required according to the capacity of scrubber machines. Wet section including sump will be made of1.25mm thick SS-304 A grade stainless steel . In addition to the above, scrubber shall be provided with adequate vibration isolation padsand fire retardent flexible canvass connections madeout of canvass sleeve.The Scrubber Machines (EAC) shall be of following duty parameters M c No Capacity S.P Motor Area to (Cfm) (mmWG) Rating be fed (HP)WS-1 28000 68-70 20.0 Kitchen Area | No | 0.00 | 1.00 |  | 0
149017 |  | INLINE FANS (Single Phase) Supply, Installation, Testing Commissioning of circular rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1phase AC power supply. Fan shall be installed as shown in the drawings and will be of following characteristics All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top necessary power cable. Fan Capacity S.P Area to No. (Cfm) (mmWG) to be exhausted IF-1(Circular) 300 14-15 Pantry | No | 0.00 | 1.00 |  | 0