## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
164332 | A | CONNECTING INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES BUILDING If any termination or connection of the unit services is required outside the site location (i.e., connection termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  | 0.00 | 0.00 |  | 0
164333 | B | HVAC EQUIPMENTS AC EQUIPMENT (CHILLED WATER - TYPE) |  | 0.00 | 0.00 |  | 0
164334 | B.1 | Supply, installation, testing and commissioning of chilled water type Medium static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3 G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping. The unit shall be suitable for 230 ± 10 volts, 50 60 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level. |  | 0.00 | 0.00 |  | 0
164335 | B.1.1 | 2.0 TR - (400 CFM @ 30-40 PASCAL -ESP) | Nos | 0.00 | 1.00 |  | 0
164336 | B.2 | Supply, installation, testing Commissioning of Air Curtains with limit switch suitable for operating in Single Phase 230 V 50 Hz power supply of the following sizes with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements. Air curtains shall be interlinked with automatic door. Height range shall be in between 2.5 m to 3.0 m. |  | 0.00 | 0.00 |  | 0
164337 | B.2.1 | Air Curtain - 1250 Length | Nos | 0.00 | 1.00 |  | 0