## PriceBidservice
SubItemUniqueCode | ItemCode | ItemName | UOM | Rate | Quantity | Remarks | SupplierRate
149018 |  | REFRIGERANT PIPING Supply, Installation,Testing Commissioning of copper refrigerant piping complete with copper fittings charge of regrigerant gas for the above split units. Piping associated with split units to be insulated with 19mm thick closed cell elastomeric insulation with Class O in tubing form as required. Piping shall be laid over duly painted slotted angle trays fixed with GI clamps. Quoted Price shall be inclusive of UV protection paint for all exposed pipes of approved make. Price shall be inclusive of copper power cabling from indoor to outdoor unit as required. Referigerant piping shall be epoxy coated to prevent erosion. |  | 0.00 | 0.00 |  | 0
149019 | a. | Pair of hard drawn copper refrigerant piping for the above split units with scroll compressor. | RM | 0.00 | 25.00 |  | 0
149020 | b. | Pair of Soft refrigerant piping for non ductable split units with rotary compressor. | RM | 0.00 | 55.00 |  | 0
149021 | 1 | MS FRAME FOR ODUs Supply and Erection of MS base frame duly applied with red-oxide primer followed by black enamel paint for mounting of outdoor units. | Kg | 0.00 | 55.00 |  | 0
149022 | 2 | PIPING CONDENSATE DRAIN PIPING -cPVC Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class O fire retardant properties in tubing form . Pipes shall be of following sizes |  | 0.00 | 0.00 |  | 0
149023 | a. | 50mm dia | RM | 0.00 | 5.00 |  | 0
149024 | b. | 40mm dia | RM | 0.00 | 10.00 |  | 0
149025 | c. | 32mm dia | RM | 0.00 | 2.00 |  | 0
149026 | d. | 25mm dia | RM | 0.00 | 5.00 |  | 0
149027 | 3 | DUCTWORK AIR TERMINALS FACTORY FABRICATED DUCTING Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI C channels, GI C channels etc. as approved by clients consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle channel arrangement as required for ducts being installed outside or within building wherever required. Spacing between duct supports should not exceed 2m. All duct support to be provided with check nuts (lock nuts). While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs. |  | 0.00 | 0.00 |  | 0
149028 | a. | 1mm to 899mm -- 26G GSS with TDC Joints | SqM | 0.00 | 5.00 |  | 0
149029 | b. | 900mm to 1200mm -- 24G GSS with TDC Joints | SqM | 0.00 | 10.00 |  | 0
149030 | c. | 1201mm to 1800mm - 22G GSS with TDC Joints | SqM | 0.00 | 5.00 |  | 0
149031 | 3.2 | SITE FABRICATED DUCTING Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications |  | 0.00 | 0.00 |  | 0
149032 |  | a. 0.63mm (24 gauge) GSS | SqM | 0.00 | 10.00 |  | 0
149033 |  | b. 0.8 mm (22 gauge) GSS | SqM | 0.00 | 5.00 |  | 0
149034 | 3.3 | FLEXIBLE CANVASS CONNECTIONS Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units ductable split units inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame flange on both sides of approved make. | RM | 0.00 | 4.00 |  | 0
149035 | 3.4 | LINEAR GRILLES Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. i. 100 150 200 250 mm High grilles | SqM | 0.00 | 1.00 |  | 0
149036 | 3.5 | DOUBLE LOUVERED GRILLES Supply, Installation ,Testing and Balancing of double louvered supply air grilles as per approved shop drawings and specifications complete with key operated aluminium volume control dampers. a. Powder coated extruded aluminium grilles. | SQM | 0.00 | 0.50 |  | 0
149037 | 3.6 | AIR TRANSFER GRILLES Supply, Installation and Testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets pantry. | SQM | 0.00 | 0.20 |  | 0
149038 | 3.7 | Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings.- For Rectangular Duct | SqM | 0.00 | 0.50 |  | 0
149039 | 3.8 | Supply, Installation and Testing of GI multi blade type louver dampers as per the specifications and shop drawings. | SqM | 0.00 | 1.00 |  | 0
149040 | 4.1 | INSULATION ACOUSTIC LINING OF DUCTS Using Open Cell Nitrile Rubber Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. Adhesive used shall be Low VOC type. 10mm thick lining | SqM | 0.00 | 5.00 |  | 0
149041 | 4.2 | INSULATION ACOUSTIC LINING OF DUCTS Using Fibre Glass Supply and Application of internal acoustic lining of supply return air ducting using resin bonded fibre glass insulation of density not less than 32Kg CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated sheet etc. as required for complete installation. a. 25mm thick lining | SqM | 0.00 | 10.00 |  | 0
149042 | 5 | THERMAL INSULATION OF DUCTS (Using Factory Laminated aluminium foil faced,Class O Closed Cell Elastomeric insulation) Supply and Application of internal external thermal insulation of supply return air ducting using closed cell elastomeric insulation with class O fire retardant properties as per the specifications and drawings.Adhesive used shall be Low VOC type. a. 13mm thick insulation | SQM | 0.00 | 30.00 |  | 0
149043 | 6 | AIR CURTAIN Supply , Installation and Testing of air curtains with noiseless, statically dynamically balanced aluminium blowers, cleanable type pre-filters, motor powder coated aluminium enclosure as per the specifications. Unit shall be complete with Plug Top necessary power cable. |  | 0.00 | 0.00 |  | 0
149044 | b. | 2.1 M long air curtain | No | 0.00 | 1.00 |  | 0
149045 | c. | 1.5 M long air curtain | No | 0.00 | 2.00 |  | 0
149046 | 7 | DUCTWORK AIR TERMINALS - INCLUDING IN SECTION A FACTORY FABRICATED DUCTING Supply, Installation and Testing of factory fabricated GSS ducting complete with vanes,splitter dampers, fire retardant gaskets, hanging arrangement including fully threaded GI rods and GI C channels rolled steel wires or Gripple Wire Rope Hangers Supports complete with end fixing, GI C channels etc. as approved by clients consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply exhaust air ducts outside or within building wherever required. Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI C channels Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct MS angle. All duct supports shall be provided with check nuts (lock nuts). While selecting the duct supports vendor shall ensurevibration free installation.Quoted price shall be inclusive of smoke test using smoke bombs. For Air-Cooling ducts |  | 0.00 | 0.00 |  | 0
149047 | a. | 1mm to 899mm -- 24G GSS with TDC Joints | SqM | 0.00 | 50.00 |  | 0
149048 | b. | 900mm to 1500mm -- 22G GSS with TDC Joints | SqM | 0.00 | 50.00 |  | 0
149049 | c. | 1501mm to 2100mm - 20G GSS with TDC Joints | SqM | 0.00 | 10.00 |  | 0
149050 | 7.1 | SITE FABRICATED DUCTING Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications. |  | 0.00 | 0.00 |  | 0
149051 | a. | a. 0.63mm (24 gauge) GSS | SqM | 0.00 | 15.00 |  | 0
149052 | b. | b. 0.8 mm (22 gauge) GSS | SqM | 0.00 | 5.00 |  | 0
149053 | c. | c. 1.0mm (20 gauge) GSS | SqM | 0.00 | 5.00 |  | 0
149054 | 7.2 | For Kitchen Exhaust Supply, fabrication, Installation and testing of MS ductingfor kitchen exhaust contructed out of 2mm thick MS sheet using MS angle iron flanges in line with good engineering practice. Entire ducting shall be applied with minimum two coats of red oxide primer. Duct shall be provided with oil trap as required | SqM | 0.00 | 140.00 |  | 0
149055 | 7.3 | FLEXIBLE CANVASS CONNECTIONS Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units ductable split units inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame flange on both sides of approved make. | RM | 0.00 | 8.50 |  | 0
149056 | 7.4 | LINEAR GRILLES Supply, Installation , Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour shade. Powder coated aluminium grilles of extruded sections with integral flanges on both sides ends as required complete with corner pieces. i. 100 150 200 250 mm High grilles | SqM | 0.00 | 8.00 |  | 0
149057 | 8 | AIR TRANSFER GRILLES Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings. | SQM | 0.00 | 3.50 |  | 0
149058 | 9 | Supply, Installation and Testing of Aluminium multi bladetype louver dampers as per the specifications and shop drawings. | SqM | 0.00 | 6.00 |  | 0
149059 | 10 | Supply, Installation and Testing of fresh air powdered coated anodised extruded aluminium louvers to be installed outside for suction ( airwashers), as per approved shop drawings and specifications. Sample of louvers to be got approved from consultants and Clients prior to procurement. | SqM | 0.00 | 1.00 |  | 0
149060 | 11 | Supply, Installation and Testing of Bird Screens with GI wire mesh to be installed at the suction of fresh air discharge of Exhaust air as per the specifications and shop drawings.Sample of bird screen to be got approved from consultants and Clients prior to procurement. | SqM | 0.00 | 1.00 |  | 0
149061 | 12 | INSULATION THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) (Using Factory Laminated fibre glass insulation) Supply and Application of external thermal insulation of supply return air ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Quoted price shall be inclusive of Low VOC adhesive as required, aluminium tape straps. 50mm thick insulation | SqM | 0.00 | 140.00 |  | 0
149062 | 13 | THERMAL INSULATION OF DUCTS-(FOR AIR SCRUBBER DUCT) - EXPOSED (Using Factory Laminated fibre glass insulation) Supply and Application of external thermal insulation of supply return air ducting using aluminium foil faced fibre glass insulation of density not less than 24Kg CuM and aluminium foil thickness of 22 microns as per the specifications and drawings. Quoted price shall be inclusive of Low VOC adhesive as required, aluminium tape straps. Insulation shall be covered necessary glass cloth UV protection paint. 50mm thick insulation | SqM | 0.00 | 15.00 |  | 0
149063 | a. | THERMAL INSULATION OF DUCTS - Air Washer (Using aluminium foil faced Class O Fire Retardant Properties Closed Cell Elastomeric insulation) Supply and Application of external thermal insulation of supply return air ducting using factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class O fire retardant properties as per the specifications and drawings. aluminium foil face shall provide protection from mechanical impact, and Scratches etc. Both insulation aluminium foil layer should have built in antimicrobial protection. Expose insulation shall be covered with necessary glass cloth UV protection paint. Adhesive - AC Duct King Eco Fresh 25mm thick insulation - For AC Duct in Kitchen | SqM | 0.00 | 135.00 |  | 0
149064 | 14 | KVF PANEL -1 (Location Kitchen ) - 13.8KW For 9700Cfm Air Washers Pump, 12100Cfm SISW Fan ESP Incoming 63 Amps ,TP MCCB with electronic release earth fault relay, door interlock and front drive rotor kit-- 1set(0-500) V digital Voltmeter with built in Selectorswitch -- 1setDigital Ammeter with built in selector switch- 1setCurrent Transformers - 1setLED type RYB phase indication lights- 1setBusbar100 Amps TPN aluminium busbar havingsuitable fault level, with PVC heat shrunk sleeves on SMC DMC supports. | No | 0.00 | 1.00 |  | 0
149065 | 15 | CABLING Supply, laying, affecting connections andarmoured PVC insulated aluminium copperconductor cables. Cables shall be inclusive ofall clamps, saddles, screws, cable identificationtags, cable terminal joints including terminallugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted priceshall be inclusive of perforated duly painted2mm thick MS trays to be installed inside and8SWG copper earth wire for all equipment.EQUIPMENT |  | 0.00 | 0.00 |  | 0
149066 | a. | 3 C x 10 Sqmm cable (Copper) | RM | 0.00 | 10.00 |  | 0
149067 | b. | 3 C x 6 Sqmm cable (Copper) | RM | 0.00 | 20.00 |  | 0
149068 | c. | 3 C x 2.5 Sqmm cable (Copper) | RM | 0.00 | 5.00 |  | 0
149069 | d. | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM | 0.00 | 5.00 |  | 0
149070 | e | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM | 0.00 | 10.00 |  | 0
149071 | 16 | Supply and fixing of 1.1 KV grade rubbermat 914.4 mm wide 6mm thick to withstand 1.1 KV dielectric strength in front of each panel. | RM | 0.00 | 2.00 |  | 0
149072 | 17 | Supply, Installation Testing of TPN isolator in weather proof enclosure near fans | No | 0.00 | 2.00 |  | 0