## HVAC
NAME OF PROJECT: Food Court at Eklera
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
A | EQUIPMENTS
1 | AIR SCRUBBER
Modular Double skin Floor mounted air scrubber units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet & 0.8mm thick Plain GI (270gsm) inner sheet comprising of Intake section for duct connection, Al Wiremesh filter section, Wet section made of 20g SS Tank, Three Phase Pump (1w+1s), GI internal piping, Single Bank Spray Nozzles and 2bend PVC eliminators. Blower section with DIDW Aerofoil/ Backward/ Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type & suitable for VFD operation) & LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual / motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates/Casing/blank offs of Eliminators shall also be made of SS.
1.1 | 6000 CFM (65mm of wg Total St. Pressure) | No. | 1 | 178000 | 178000
2 | AIR WASHER
Modular Double skin Floor mounted air washer units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet & 0.8mm thick Plain GI (270gsm) inner sheet comprising of Al Wiremesh filter section, Wet section made of 20g SS Tank, Single Phase Pump (1w+1s), PVC internal piping, Distribution system, 200mm deep Cellulose Pads & 2 bend PVC eliminators. Blower section with DIDW Aerofoil/ Backward/ Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type & suitable for VFD operation) & LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual / motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates/Casing/blank offs of Pads & Eliminators shall also be made of SS.
2.1 | 5000 CFM (50mm of wg Total St. Pressure) | No. | 1 | 155000 | 155000
B | AIR DISTRIBUTION
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 18 G sheet | sq.m | 25 | 2300 | 57500
| 20G sheet | sq.m | 5 | 2050 | 10250
| 22G sheet | sq.m | 5 | 1850 | 9250
| 24G sheet | sq.m | 40 | 1600 | 64000
| 26G sheet | sq.m | 5 | 1400 | 7000
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 18 G sheet | sq.m | 5 | 2000 | 10000
| 20G sheet | sq.m | 5 | 1750 | 8750
| 22G sheet | sq.m | 5 | 1400 | 7000
| 24G sheet | sq.m | 5 | 1200 | 6000
3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 1 | 120000 | 120000
4 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1 | 9500 | 9500
5 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 2 | 4500 | 9000
6 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.1 | 12000 | 1200
7 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | SQMT | 0.1 | 12000 | 1200
C | THERMAL INSULATION
1 | THERMAL INSULATION FOR KITCHEN DUCTS
SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade.
| 80 mm Thick | sq.m | 30 | 850 | 25500
D | ELECTRICAL INSTALLATION
1 | CONTROL PANEL FOR AHU / Air washer / Scrubber (WITH DOL / SD STARTER)
Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing & terminating into MCCB in each panel shall be provided by the electrical contractor.
All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included.
All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System.
The panel shall include the following components and accessories.
a. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA.
b. | DOL / SD starter as per HP ratings
c. | Terminal block for power distribution.
d. | Contactor, over load relay with built in single phasing protection.
e. | Phase indicating lights and indicating light for ON status.
f. | Digital voltmeter and digital ammeter with selector switches.
g. | Time delay relay for delayed automatic restart of air handling unit motor.
h | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
i | All starters shall be provided with suitable potential free contract for connections to the Building Automation System.
The number of AHU control panels shall be as follows.
| 3 HP DOL Starter | No. | 1 | 28000 | 28000
| 5 HP DOL Starter | No. | 1 | 35000 | 35000
GRAND TOTAL |  |  |  |  | 742150