## Price Comparison
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | Comp. Date : 23/12/2024 | Comp. Date : 23/12/2024 | Comp. Date : 23/12/2024 | Vendor Name : STAR AND MERIT INTERIORS PRIVATE LIMITEDND (RV242523805) | [5 empty] | Vendor Name : Electech Enterprises (RV232422514) | [5 empty] | Vendor Name : Arrow Electrical (RV242522534)
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ #: R2461 | RFQ #: R2461 | RFQ #: R2461 | Contact Name : MUJEEB | [5 empty] | Contact Name : Alam | [5 empty] | Contact Name : SANTOSH KHAKE
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ Date : 18/12/2024 11:22:49 | RFQ Date : 18/12/2024 11:22:49 | RFQ Date : 18/12/2024 11:22:49 | Vendor City : | [5 empty] | Vendor City : | [5 empty] | Vendor City :
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | BCD Date : 21/12/2024 13:53:00 | BCD Date : 21/12/2024 13:53:00 | BCD Date : 21/12/2024 13:53:00 | Telephone # : | [5 empty] | Telephone # : | [5 empty] | Telephone # :
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT |  |  |  | Mobile # : | [5 empty] | Mobile # : | [5 empty] | Mobile # :
PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | Email : starsandmerit@gmail.com | [5 empty] | Email : alam@electechenterprises.net | [5 empty] | Email : project.arrowelectricals@gmail.com
Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Round # : 1 (RFQ) | [5 empty] | Round # : 1 (RFQ) | [5 empty] | Round # : 1 (RFQ)
Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Buyer : Abdul Rehman / Technical : / Approver : | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date : |  |  | Quotation Date : |  |  | Quotation Validity Date :
Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Currency :INR | Currency :INR | Currency :INR | Buyer Remark : | [5 empty] | Buyer Remark : | [5 empty] | Buyer Remark :
Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | BUDGET PRICE : | .00 |  | Quote Currency : INR | [5 empty] | Quote Currency : INR | [5 empty] | Quote Currency : INR
# | Item Code | Item Description | Unit | Qty | Last PO Details | Lowest Unit Rate | Lowest Vendor | Price | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total | Price | Disc % | GST % | Technical | Unit Price | Total
1 | Electrical | Electrical | NOS | 1.00 |  | 610040.00 | STAR AND MERIT INTERIORS PRIVATE LIMITEDND | 610040.00 | 0.00 | 18.00 |  | 610,040.00 | 610,040.00 | 710370.00 | 0.00 | 18.00 |  | 710,370.00 | 710,370.00 | 702670.00 | 0.00 | 18.00 |  | 702,670.00 | 702,670.00
2 | FAS | FAS | NOS | 1.00 |  | 46930.00 | STAR AND MERIT INTERIORS PRIVATE LIMITEDND | 46930.00 | 0.00 | 18.00 |  | 46,930.00 | 46,930.00 | 62200.00 | 0.00 | 18.00 |  | 62,200.00 | 62,200.00 | 74260.00 | 0.00 | 18.00 |  | 74,260.00 | 74,260.00
Item Total | [8 empty] | .00 | 118,254.60 |  |  | 656,970.00 |  | .00 | 139,062.60 |  |  | 772,570.00 |  | .00 | 139,847.40 |  |  | 776,930.00
Discount Total Value | [7 empty] | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00 | Grand Dis. Amt | .00 |  |  |  | .00
GST Total Amount | [12 empty] | 118,254.60 | [5 empty] | 139,062.60 | [5 empty] | 139,847.40
Net Landed Cost | [11 empty] | INR | 775,224.60 |  |  |  |  | INR | 911,632.60 |  |  |  |  | INR | 916,777.40
Vendor Status | [7 empty] | Round # : 1 (RFQ) | Round # : 1 (RFQ)
Sr No. | Vendor Code | Vendor Name | [5 empty] | Status | Remarks
1 | RV242523688 | RUDRA INTERIORS POINT PVT. LTD. | [5 empty] | Participate
2 | RV242523803 | SHAH ENTERPRISES | [5 empty] | Not Participate
3 | RV232422514 | Electech Enterprises | [5 empty] | Participate
4 | RV242523805 | STAR AND MERIT INTERIORS PRIVATE LIMITEDND | [5 empty] | Participate
5 | RV242522534 | Arrow Electrical | [5 empty] | Participate

## BOQ Price Bid
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | Comp. Date : 23/12/2024 | Comp. Date : 23/12/2024 | Comp. Date : 23/12/2024 | Vendor Name : STAR AND MERIT INTERIORS PRIVATE LIMITEDND | Vendor Name : STAR AND MERIT INTERIORS PRIVATE LIMITEDND | Vendor Name : Electech Enterprises | Vendor Name : Electech Enterprises | Vendor Name : Arrow Electrical | Vendor Name : Arrow Electrical
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ #: R2461 | RFQ #: R2461 | RFQ #: R2461 | Contact Name : MUJEEB | Contact Name : MUJEEB | Contact Name : Alam | Contact Name : Alam | Contact Name : SANTOSH KHAKE | Contact Name : SANTOSH KHAKE
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ Date : 18/12/2024 11:22:49 | RFQ Date : 18/12/2024 11:22:49 | RFQ Date : 18/12/2024 11:22:49 | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City : | Vendor City :
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | BCD Date : 21/12/2024 13:53:00 | BCD Date : 21/12/2024 13:53:00 | BCD Date : 21/12/2024 13:53:00 | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # : | Telephone # :
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT |  |  |  | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # : | Mobile # :
PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | Email : starsandmerit@gmail.com | Email : starsandmerit@gmail.com | Email : alam@electechenterprises.net | Email : alam@electechenterprises.net | Email : project.arrowelectricals@gmail.com | Email : project.arrowelectricals@gmail.com
Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 1 (RFQ) | Round # : 1 (RFQ)
Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score : | Techanical Score :
Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Currency :INR | Currency :INR | Currency :INR | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date : | Quotation Date :
Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | BUDGET PRICE :.00 | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date : | Quotation Validity Date :
Sr No. | Item Code | Item Name | Item Description | UOM | Qty | Minimum Amount | Unit Price | Amount | Unit Price | Amount | Unit Price | Amount
1 | Electrical | Electrical | Electrical | NOS | 1.000 |  |  | 610,040.00 |  | 710,370.00 |  | 702,670.00
1 | A | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING
2 | A.1 | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement.
3 | B | METER METER PANEL | METER METER PANEL
4 | B.1 | Supply, Installation, Testing Commissioning of kWH MFM Energy Meter Panel complete with Enclosure (If required as per site condition Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type and compatible with Airport BMS for realtime monitoring, of approved make or any other make with kVAH option with Approval from TS Department. | Supply, Installation, Testing Commissioning of kWH MFM Energy Meter Panel complete with Enclosure (If required as per site condition Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type and compatible with Airport BMS for realtime monitoring, of approved make or any other make with kVAH option with Approval from TS Department.
5 | B.1.1 | 100 5A Energy Meter(Direct)-3 Phase | 100 5A Energy Meter(Direct)-3 Phase | Nos | 1.000 | 17,000.00 | 17000.00 | 17,000.00 | 25000.00 | 25,000.00 | 22500.00 | 22,500.00
6 | C | LV CABLING | LV CABLING
7 | C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing.
8 | C.1.1 | 3.5C x 50 Sq. mm XLPE AL Armoured Cable + 2 x 8 SWG CU. | 3.5C x 50 Sq. mm XLPE AL Armoured Cable + 2 x 8 SWG CU. | Mtr | 15.000 | 7,950.00 | 980.00 | 14,700.00 | 530.00 | 7,950.00 | 610.00 | 9,150.00
9 | C.1.2 | 4C x 4 Sq. mm XLPE CU. Armoured Cable + 10 SWG CU. | 4C x 4 Sq. mm XLPE CU. Armoured Cable + 10 SWG CU. | Mtr | 45.000 | 19,260.00 | 670.00 | 30,150.00 | 550.00 | 24,750.00 | 428.00 | 19,260.00
10 | D | CABLE END TERMINATIONS | CABLE END TERMINATIONS
11 | D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete. | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete.
12 | D.1.1 | 3.5C x 50 Sq. mm XLP Al. Armoured Cable | 3.5C x 50 Sq. mm XLP Al. Armoured Cable | Nos | 4.000 | 2,120.00 | 1600.00 | 6,400.00 | 530.00 | 2,120.00 | 750.00 | 3,000.00
13 | D.1.2 | 4C x 4 Sq. mm XLPE CU Armoured Cable | 4C x 4 Sq. mm XLPE CU Armoured Cable | Mtr | 4.000 | 1,120.00 | 600.00 | 2,400.00 | 550.00 | 2,200.00 | 280.00 | 1,120.00
14 | E | DISTRIBUTION BOARDS | DISTRIBUTION BOARDS
15 | E.1 | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement).
16 | E.1.1 | LPDB-01 | LPDB-01 | Each | 1.000 | 48,000.00 | 48000.00 | 48,000.00 | 165000.00 | 165,000.00 | 140000.00 | 140,000.00
17 |  | 16 Way Three phase Panel board | 16 Way Three phase Panel board
18 |  | Incomer | Incomer
19 |  | 100A TP MCCB - 1 No. | 100A TP MCCB - 1 No.
20 |  | Outgoings | Outgoings
21 |  | 10 16 20 25A SP MCB- 42 Nos | 10 16 20 25A SP MCB- 42 Nos
22 |  | 25A 4P RCBO 30mA - 2 No. | 25A 4P RCBO 30mA - 2 No.
23 | F | LIGHT POINT WIRING | LIGHT POINT WIRING
24 | F.1 | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension.
25 | F.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. | 1 No. light point controlled by 1 No 10A, SP Switch. | Nos | 4.000 | 10,000.00 | 3400.00 | 13,600.00 | 2500.00 | 10,000.00 | 4050.00 | 16,200.00
26 | F.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) | Secondary light points. (from the first light point without supply and installation of switches.) | Nos | 16.000 | 16,000.00 | 2300.00 | 36,800.00 | 1000.00 | 16,000.00 | 1850.00 | 29,600.00
27 | G | CIRCUIT WIRING | CIRCUIT WIRING
28 | G.1 | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires.
29 | G.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. | Mtr | 450.000 | 126,900.00 | 290.00 | 130,500.00 | 350.00 | 157,500.00 | 282.00 | 126,900.00
30 | G.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points. | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points. | Mtr | 200.000 | 52,000.00 | 260.00 | 52,000.00 | 450.00 | 90,000.00 | 385.00 | 77,000.00
31 | H | POWER POINTS (SWITCHES SOCKETS) | POWER POINTS (SWITCHES SOCKETS)
32 | H.1 | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply.
33 | H.1.1 | 13A Single Switched Socket Outlet | 13A Single Switched Socket Outlet | Nos | 28.000 | 21,000.00 | 850.00 | 23,800.00 | 750.00 | 21,000.00 | 750.00 | 21,000.00
34 | H.1.2 | 13A Dual Switched Socket Outlet | 13A Dual Switched Socket Outlet | Nos | 2.000 | 1,560.00 | 780.00 | 1,560.00 | 1500.00 | 3,000.00 | 1410.00 | 2,820.00
35 | H.1.3 | 16A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) | 16A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) | Nos | 7.000 | 19,600.00 | 3900.00 | 27,300.00 | 2800.00 | 19,600.00 | 3550.00 | 24,850.00
36 | H.1.4 | 20A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) | 20A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) | Nos | 6.000 | 18,000.00 | 4500.00 | 27,000.00 | 3000.00 | 18,000.00 | 4500.00 | 27,000.00
37 | H.1.5 | 20A Unswitched Fused Connection Outlet with-out Neon Indicator. | 20A Unswitched Fused Connection Outlet with-out Neon Indicator. | Nos | 6.000 | 5,100.00 | 900.00 | 5,400.00 | 1000.00 | 6,000.00 | 850.00 | 5,100.00
38 | H.1.6 | 20A Double Pole Switch with Neon indicator | 20A Double Pole Switch with Neon indicator | Nos | 2.000 | 2,100.00 | 1200.00 | 2,400.00 | 1050.00 | 2,100.00 | 1510.00 | 3,020.00
39 | H.1.7 | 25A Three Phase Industrial Switched Socket (5 Pin) (Wall Mounted Metal Clad Socket) | 25A Three Phase Industrial Switched Socket (5 Pin) (Wall Mounted Metal Clad Socket) | Nos. | 2.000 | 9,800.00 | 4900.00 | 9,800.00 | 12000.00 | 24,000.00 | 14500.00 | 29,000.00
40 | H.1.8 | 20A Isolator with suitable metal enclosure | 20A Isolator with suitable metal enclosure | Nos. | 4.000 | 6,000.00 | 3800.00 | 15,200.00 | 1500.00 | 6,000.00 | 4500.00 | 18,000.00
41 | H.1.9 | One Gang Blank Plate | One Gang Blank Plate | Nos | 2.000 | 200.00 | 120.00 | 240.00 | 100.00 | 200.00 | 350.00 | 700.00
42 | J | CONTAINMENT | CONTAINMENT
43 | J.1 | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings. | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings.
44 | J.1.1 | 300 x 50 mm Cable Tray | 300 x 50 mm Cable Tray | Mtr. | 20.000 | 29,000.00 | 1700.00 | 34,000.00 | 1450.00 | 29,000.00 | 1632.00 | 32,640.00
45 | J.1.2 | 150 x 50 mm Cable Tray | 150 x 50 mm Cable Tray | Mtr. | 30.000 | 18,000.00 | 980.00 | 29,400.00 | 600.00 | 18,000.00 | 1045.00 | 31,350.00
46 | L | DATA NETWORK SYSTEM | DATA NETWORK SYSTEM
47 | L.1 | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension.
48 | L.1.1 | Single Data outlet (RJ45) Jack | Single Data outlet (RJ45) Jack | Nos | 3.000 | 1,650.00 | 800.00 | 2,400.00 | 550.00 | 1,650.00 | 750.00 | 2,250.00
49 | L.1.2 | Dual Data outlet (RJ45) Jack | Dual Data outlet (RJ45) Jack | Nos | 2.000 | 1,300.00 | 800.00 | 1,600.00 | 650.00 | 1,300.00 | 1250.00 | 2,500.00
50 | L.1.3 | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | Mtr. | 180.000 | 39,600.00 | 300.00 | 54,000.00 | 220.00 | 39,600.00 | 227.00 | 40,860.00
51 | M | PA SYSTEM | PA SYSTEM
52 | M.1 | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension.
53 | M.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories | 6 Watts ceiling mount Speaker with all the necessary accessories | Nos | 1.000 | .00 | 2900.00 | 2,900.00 | 2500.00 | 2,500.00 | 0.00 | .00
54 | M.1.2 | Volume Controller | Volume Controller | Nos | 1.000 | .00 | 1800.00 | 1,800.00 | 500.00 | 500.00 | 0.00 | .00
55 | M.1.3 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | Mtr. | 30.000 | 6,600.00 | 245.00 | 7,350.00 | 250.00 | 7,500.00 | 220.00 | 6,600.00
56 | N | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS
57 | N.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements. | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements.
58 | N.1.1 | Labelling Tagging for Services and Equipment s | Labelling Tagging for Services and Equipment s | Lot | 1.000 | 5,000.00 | 7800.00 | 7,800.00 | 5000.00 | 5,000.00 | 5000.00 | 5,000.00
59 | O | MISCELLANEOUS | MISCELLANEOUS
60 | O.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
61 | O.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Unit | 1.000 | 2,200.00 | 2200.00 | 2,200.00 | 3000.00 | 3,000.00 | 3000.00 | 3,000.00
62 | O.1.2 | Provide and Fixing Shock Treatment Chart | Provide and Fixing Shock Treatment Chart | Unit | 1.000 | 1,450.00 | 1450.00 | 1,450.00 | 1500.00 | 1,500.00 | 1500.00 | 1,500.00
63 | O.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side | Provide and Fixing of L.T. danger sign boards in Panel side | Unit | 1.000 | 400.00 | 890.00 | 890.00 | 400.00 | 400.00 | 750.00 | 750.00
2 | FAS | FAS |  | NOS | 1.000 |  |  | 46,930.00 |  | 62,200.00 |  | 74,260.00
64 | C | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE ) | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE )
65 |  | FIRE ALARM SYSTEM - DETECTION DEVICES | FIRE ALARM SYSTEM - DETECTION DEVICES
66 | C.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles with all necessary mounting and fixing arrangements. (Above Below Ceiling) | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles with all necessary mounting and fixing arrangements. (Above Below Ceiling)
67 | C.1.1 | Below ceiling level | Below ceiling level | Nos | 2.000 | 9,120.00 | 4560.00 | 9,120.00 | 6500.00 | 13,000.00 | 7100.00 | 14,200.00
68 | C.1.2 | Above ceiling level | Above ceiling level | Nos | 2.000 | 9,120.00 | 4560.00 | 9,120.00 | 6500.00 | 13,000.00 | 7100.00 | 14,200.00
69 | C.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements.
70 | C.2.1 | Heat Detector - 58°C fixed temperature | Heat Detector - 58°C fixed temperature | Nos | 1.000 | 3,900.00 | 3900.00 | 3,900.00 | 7000.00 | 7,000.00 | 8200.00 | 8,200.00
71 | C.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements.
72 | C.3.1 | Manual Call Point - (Wall Partition Mounted) | Manual Call Point - (Wall Partition Mounted) | Nos | 1.000 | 3,700.00 | 3700.00 | 3,700.00 | 7000.00 | 7,000.00 | 9800.00 | 9,800.00
73 | C.4 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements.
74 | C.4.1 | Response Indicator Remote Indicator | Response Indicator Remote Indicator | Nos | 2.000 | 300.00 | 270.00 | 540.00 | 150.00 | 300.00 | 1250.00 | 2,500.00
75 |  | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES
76 | C.5 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles. | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles.
77 | C.5.1 | Sounder Strobe - (Wall Partition Mounted) | Sounder Strobe - (Wall Partition Mounted) | Nos | 1.000 | 3,700.00 | 3700.00 | 3,700.00 | 9000.00 | 9,000.00 | 10800.00 | 10,800.00
78 |  | FIRE ALARM SYSTEM - MODULE DEVICES | FIRE ALARM SYSTEM - MODULE DEVICES
79 | C.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements.
80 | C.6.1 | Isolator Module | Isolator Module | Nos | 1.000 | 5,600.00 | 5600.00 | 5,600.00 | 7500.00 | 7,500.00 | 6910.00 | 6,910.00
81 |  | FIRE ALARM SYSTEM - CABLING | FIRE ALARM SYSTEM - CABLING
82 | C.7 | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements. | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements.
83 | C.7.1 | 2C x 1.5 Sq. mm Cu Cable | 2C x 1.5 Sq. mm Cu Cable | Mtr | 45.000 | 5,400.00 | 250.00 | 11,250.00 | 120.00 | 5,400.00 | 170.00 | 7,650.00

## Technical Score Detail
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | Comp. Date : 23/12/2024 | Comp. Date : 23/12/2024 | Comp. Date : 23/12/2024 | Vendor Name : STAR AND MERIT INTERIORS PRIVATE LIMITEDND |  | Vendor Name : Electech Enterprises |  | Vendor Name : Arrow Electrical
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ #: R2461 | RFQ #: R2461 | RFQ #: R2461 | Contact Name : MUJEEB |  | Contact Name : Alam |  | Contact Name : SANTOSH KHAKE
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ Date : 18/12/2024 11:22:49 | RFQ Date : 18/12/2024 11:22:49 | RFQ Date : 18/12/2024 11:22:49 | Vendor City : |  | Vendor City : |  | Vendor City :
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | BCD Date : 21/12/2024 13:53:00 | BCD Date : 21/12/2024 13:53:00 | BCD Date : 21/12/2024 13:53:00 | Telephone # : |  | Telephone # : |  | Telephone # :
|  | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT | RFQ No: R2461 COST COMPARISON REPORT |  |  |  | Mobile # : |  | Mobile # : |  | Mobile # :
PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | PR Number : QMT-2425-00080,QMT-2425-00083 | Email : starsandmerit@gmail.com |  | Email : alam@electechenterprises.net |  | Email : project.arrowelectricals@gmail.com
Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Package / RFQ Name : TFAS / RFQ / QMT-2425-00080,QMT-2425-00083 | Round # : 1 (RFQ) |  | Round # : 1 (RFQ) |  | Round # : 1 (RFQ)
Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Buyer : Abdul Rehman | Quotation Date : |  | Quotation Date : |  | Quotation Date :
Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Currency :INR | Currency :INR | Currency :INR | Quotation Validity Date : |  | Quotation Validity Date : |  | Quotation Validity Date :
Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | Comp. # : 1 | BUDGET PRICE : | .00 |  | Quote Currency : |  | Quote Currency : |  | Quote Currency :
# | Item Code | Item Description | Last PO Details | Unit | Qty | Last PO Unit Rate | Last PO Total Value | Score | Justification | Score | Justification | Score | Justification
1 | Electrical | Electrical |  | NOS | 1.000 | 0.00 | 0.00
2 | A | CONNECTING INTEGRATING UNIT M E SERVICES TO AIRPORT M E SERVICES BUILDING |  |  | 0.000 | 0.00 | 0.00
3 | A.1 | If any termination connection of the unit services are required outside the site location (i.e. connection of the unit M E to the airport M E or service termination to the airport external façade roof etc.); then the contractor has to work in consultation with the airport to plan, design detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. |  |  | 0.000 | 0.00 | 0.00
4 | B | METER METER PANEL |  |  | 0.000 | 0.00 | 0.00
5 | B.1 | Supply, Installation, Testing Commissioning of kWH MFM Energy Meter Panel complete with Enclosure (If required as per site condition Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type and compatible with Airport BMS for realtime monitoring, of approved make or any other make with kVAH option with Approval from TS Department. |  |  | 0.000 | 0.00 | 0.00
6 | B.1.1 | 100 5A Energy Meter(Direct)-3 Phase |  | Nos | 1.000 | 0.00 | 0.00
7 | C | LV CABLING |  |  | 0.000 | 0.00 | 0.00
8 | C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed, Copper conductor, Steel Tape Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD Load Calculation Sheet (Main Cable) Unarmoured Single Core Wire (ECC). The cable shall be laid Underground on Cable Tray through Cable Trunking in Pipe on Wall Trench using necessary supporting clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing. |  |  | 0.000 | 0.00 | 0.00
9 | C.1.1 | 3.5C x 50 Sq. mm XLPE AL Armoured Cable + 2 x 8 SWG CU. |  | Mtr | 15.000 | 0.00 | 0.00
10 | C.1.2 | 4C x 4 Sq. mm XLPE CU. Armoured Cable + 10 SWG CU. |  | Mtr | 45.000 | 0.00 | 0.00
11 | D | CABLE END TERMINATIONS |  |  | 0.000 | 0.00 | 0.00
12 | D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete. |  |  | 0.000 | 0.00 | 0.00
13 | D.1.1 | 3.5C x 50 Sq. mm XLP Al. Armoured Cable |  | Nos | 4.000 | 0.00 | 0.00
14 | D.1.2 | 4C x 4 Sq. mm XLPE CU Armoured Cable |  | Mtr | 4.000 | 0.00 | 0.00
15 | E | DISTRIBUTION BOARDS |  |  | 0.000 | 0.00 | 0.00
16 | E.1 | Supply, Installation, Testing Commissioning of approved make Surface Flush Floor mounting 10kA 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB s must named as per the SLD Load Calculation Sheet. Laminated SLD Load Calculation Sheet shall be placed near to DB Locations. The RCCB RCBO shall be Hpi Si series MCB s shall be B C Curve (As per Airport requirement). |  |  | 0.000 | 0.00 | 0.00
17 | E.1.1 | LPDB-01 |  | Each | 1.000 | 0.00 | 0.00
18 |  | 16 Way Three phase Panel board |  |  | 0.000 | 0.00 | 0.00
19 |  | Incomer |  |  | 0.000 | 0.00 | 0.00
20 |  | 100A TP MCCB - 1 No. |  |  | 0.000 | 0.00 | 0.00
21 |  | Outgoings |  |  | 0.000 | 0.00 | 0.00
22 |  | 10 16 20 25A SP MCB- 42 Nos |  |  | 0.000 | 0.00 | 0.00
23 |  | 25A 4P RCBO 30mA - 2 No. |  |  | 0.000 | 0.00 | 0.00
24 | F | LIGHT POINT WIRING |  |  | 0.000 | 0.00 | 0.00
25 | F.1 | Supply, Installation, Testing Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design BOQ) with approved makes Switches Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  |  | 0.000 | 0.00 | 0.00
26 | F.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. |  | Nos | 4.000 | 0.00 | 0.00
27 | F.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) |  | Nos | 16.000 | 0.00 | 0.00
28 | G | CIRCUIT WIRING |  |  | 0.000 | 0.00 | 0.00
29 | G.1 | Supply, Installation, Testing Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660 1100V grade through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement) for the following types of wires. |  |  | 0.000 | 0.00 | 0.00
30 | G.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Light control switch box Normal Sockets. |  | Mtr | 450.000 | 0.00 | 0.00
31 | G.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit Heavy Duty PVC Conduit GI Trunking from DB to Power points. |  | Mtr | 200.000 | 0.00 | 0.00
32 | H | POWER POINTS (SWITCHES SOCKETS) |  |  | 0.000 | 0.00 | 0.00
33 | H.1 | Supply, Installation, Testing Commissioning of approved makes Devices (Switches Sockets - Face Plate Finish as approved by Architect Matching to Architecture interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface Concealed as per site condition maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50 60 Hz, AC supply as per Airport Country power supply. |  |  | 0.000 | 0.00 | 0.00
34 | H.1.1 | 13A Single Switched Socket Outlet |  | Nos | 28.000 | 0.00 | 0.00
35 | H.1.2 | 13A Dual Switched Socket Outlet |  | Nos | 2.000 | 0.00 | 0.00
36 | H.1.3 | 16A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) |  | Nos | 7.000 | 0.00 | 0.00
37 | H.1.4 | 20A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) |  | Nos | 6.000 | 0.00 | 0.00
38 | H.1.5 | 20A Unswitched Fused Connection Outlet with-out Neon Indicator. |  | Nos | 6.000 | 0.00 | 0.00
39 | H.1.6 | 20A Double Pole Switch with Neon indicator |  | Nos | 2.000 | 0.00 | 0.00
40 | H.1.7 | 25A Three Phase Industrial Switched Socket (5 Pin) (Wall Mounted Metal Clad Socket) |  | Nos. | 2.000 | 0.00 | 0.00
41 | H.1.8 | 20A Isolator with suitable metal enclosure |  | Nos. | 4.000 | 0.00 | 0.00
42 | H.1.9 | One Gang Blank Plate |  | Nos | 2.000 | 0.00 | 0.00
43 | J | CONTAINMENT |  |  | 0.000 | 0.00 | 0.00
44 | J.1 | Supply Installation of approved makes GI Conduit Heavy Duty PVC Conduit, through Wall Ceiling Floor as per drawings, complete with ISI standard accessories factory made fittings. |  |  | 0.000 | 0.00 | 0.00
45 | J.1.1 | 300 x 50 mm Cable Tray |  | Mtr. | 20.000 | 0.00 | 0.00
46 | J.1.2 | 150 x 50 mm Cable Tray |  | Mtr. | 30.000 | 0.00 | 0.00
47 | L | DATA NETWORK SYSTEM |  |  | 0.000 | 0.00 | 0.00
48 | L.1 | Supply, Installation, Testing Commissioning of approved makes Data Telephone Network System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF SERVER Rack using patch cordes, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  |  | 0.000 | 0.00 | 0.00
49 | L.1.1 | Single Data outlet (RJ45) Jack |  | Nos | 3.000 | 0.00 | 0.00
50 | L.1.2 | Dual Data outlet (RJ45) Jack |  | Nos | 2.000 | 0.00 | 0.00
51 | L.1.3 | SITC of CAT6 cable on surface concealed wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) |  | Mtr. | 180.000 | 0.00 | 0.00
52 | M | PA SYSTEM |  |  | 0.000 | 0.00 | 0.00
53 | M.1 | Supply, Installation, Testing Commissioning of approved makes PA System with required cabling through suitable size GI Conduit Heavy Duty PVC Conduit GI Trunking (Containment size Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface Concealed wiring as per site condition maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports brackets for conduit and Trunking suspension. |  |  | 0.000 | 0.00 | 0.00
54 | M.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories |  | Nos | 1.000 | 0.00 | 0.00
55 | M.1.2 | Volume Controller |  | Nos | 1.000 | 0.00 | 0.00
56 | M.1.3 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable |  | Mtr. | 30.000 | 0.00 | 0.00
57 | N | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS TAGS |  |  | 0.000 | 0.00 | 0.00
58 | N.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements. |  |  | 0.000 | 0.00 | 0.00
59 | N.1.1 | Labelling Tagging for Services and Equipment s |  | Lot | 1.000 | 0.00 | 0.00
60 | O | MISCELLANEOUS |  |  | 0.000 | 0.00 | 0.00
61 | O.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants. |  |  | 0.000 | 0.00 | 0.00
62 | O.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts |  | Unit | 1.000 | 0.00 | 0.00
63 | O.1.2 | Provide and Fixing Shock Treatment Chart |  | Unit | 1.000 | 0.00 | 0.00
64 | O.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side |  | Unit | 1.000 | 0.00 | 0.00
65 | FAS | FAS |  | NOS | 1.000 | 0.00 | 0.00
66 | C | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE ) |  |  | 0.000 | 0.00 | 0.00
67 |  | FIRE ALARM SYSTEM - DETECTION DEVICES |  |  | 0.000 | 0.00 | 0.00
68 | C.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles with all necessary mounting and fixing arrangements. (Above Below Ceiling) |  |  | 0.000 | 0.00 | 0.00
69 | C.1.1 | Below ceiling level |  | Nos | 2.000 | 0.00 | 0.00
70 | C.1.2 | Above ceiling level |  | Nos | 2.000 | 0.00 | 0.00
71 | C.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
72 | C.2.1 | Heat Detector - 58°C fixed temperature |  | Nos | 1.000 | 0.00 | 0.00
73 | C.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
74 | C.3.1 | Manual Call Point - (Wall Partition Mounted) |  | Nos | 1.000 | 0.00 | 0.00
75 | C.4 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
76 | C.4.1 | Response Indicator Remote Indicator |  | Nos | 2.000 | 0.00 | 0.00
77 |  | FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES |  |  | 0.000 | 0.00 | 0.00
78 | C.5 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB EN54 along with suitable size 2 core cable clipped to structure wall ceiling through GI or Heavy Duty PVC Conduits with suitable cable clips saddles. |  |  | 0.000 | 0.00 | 0.00
79 | C.5.1 | Sounder Strobe - (Wall Partition Mounted) |  | Nos | 1.000 | 0.00 | 0.00
80 |  | FIRE ALARM SYSTEM - MODULE DEVICES |  |  | 0.000 | 0.00 | 0.00
81 | C.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB EN54, with all necessary mounting, termination and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
82 | C.6.1 | Isolator Module |  | Nos | 1.000 | 0.00 | 0.00
83 |  | FIRE ALARM SYSTEM - CABLING |  |  | 0.000 | 0.00 | 0.00
84 | C.7 | Supply, Installation, Testing and Commissioning FRLS FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure wall ceiling through approved make GI or Heavy Duty PVC Conduits with suitable cable clips saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements. |  |  | 0.000 | 0.00 | 0.00
85 | C.7.1 | 2C x 1.5 Sq. mm Cu Cable |  | Mtr | 45.000 | 0.00 | 0.00