## Electrical
BILL OF QUANTITY FOR ELECTRICAL WORK FOR IRRISH HOUSE @ DELHI
TENDER BOQ. R0
SR. | DESCRIPTION OF ITEM | UNIT | QTY | UNIT RATE (Rs.) |  | AMOUNT (Rs.)
NO. |  |  |  | MAT. | INST. | MAT. | INST. | TOTAL
1 | PANELS / DBs
Supply and Installation of main LT panel,genarally conforming to IS 8623/IS-13947/IEC-439 front operated, dead back floor mounted , totally enclosed, compartmentalised, vermin proof,indoor, non-drawout type,power panel, fabricated out of 2/1.6mm thick CRCA sheets, fully powder coated after seven tank treatment, having gasketed & hinged cover on each cubicle with insulated door knob, incorporating horizontal and vertical copper busbars complete with all internal wiring, danger sign board, earth-bus and lugs, cable chamber, busbar chamber,aluminium anodized name plates etc.as required, including 2 nos. of 6" dia instrument cooling fan with switch and ventilation louvres with wire mesh,housing below mentioned switchgears / meters. 9W fitting with CFL lamp, switch shall be provided in each vertical section,:(Panel should conform to Form- 3b of IEC- 439) (GA drawing of the panel to be got approved from the Consultant before taking up fabrication and all panels to be factory inspected before despatch)
Notes: 1. All MCCBs shall have rotary handle
2. All MCCBs shall have phase spreader assembly on
both Line & Load ends.
3. All MCCB shall have Minimum Ics=Icu
4. Incomer shall have auxilliary ON/OFF & TRIP status contacts and the same shall be wired up
electronic trip setting to Metering Compartment)
5. The panel shall conform to Form-3b as per IEC-439
6. All MCCB to be of Schneider/ABB make
7. All MCCB to be current limiting type, LSIG
8. Incomer MCCB to be shunt trip facility
7. With DOL Starter 2.2KW & 1.5KW for air washer & exhaust fan
8. With VFD for 2.2KW & 1.5KW for air washer & exhaust fan make Selec
9.Please provide CO2,FM200/HFC-227ea gas based automatic tube detection & suppression system needs to be installed in Electrical Panel
Refer: SLD
1.1.1 | MAIN PANEL | Set | 1 |  |  | 0 | 0 | 0
1.2 | Suply and installation of Four -Tier, Multi-Way, TPN,
Distribution Board for Lighting & Power distribution, surface
mounted on wall, sheet metal fabricated,powder coated,
having dust-proof and vermin 'proof, gasketed and hinged
acrylic door with all internals such as DIN rails, neutral-link,
interconnected wiring complete with earthing lugs housing
switchgears: (IP-43 with Metal Door) Refer: SLD & DB Schedule
(Make: Legrand-Ekinoxe /Schneider)
1.2.1 | KITCHEN DB 1 (KPDB-12WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.2 | KITCHEN DB 2 (BARDB-8WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.3 | LPDB 1 (12WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.4 | UPS OUTPUT | Set | 1 |  |  | 0 | 0 | 0
1.2.4 | UPSDB (16WAY SPN) | Set | 1 |  |  | 0 | 0 | 0
1.4 | S & I of 32A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
1.5 | S & I of 16A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 2 |  |  | 0 | 0 | 0
1.6 | S & I of 40A, TP, MCB + 415 V, in powder coated sheet metal box for terminating UPS to UPS DB etc. | Nos | 2 |  |  | 0 | 0 | 0
1.7 | S & I of 20A,SP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
1.8 | S & I of 16A,SP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Set | 1 |  |  | 0 | 0 | 0
1.9 | S & I of 6/10A,SP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
1.1 | S & I of 32A,TP ELMCB 300mA, Metal clad,Power socket in powder coated metal box for supplying power to AC etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
| Sub Total of 1.0 |  |  |  |  | 0 | 0 | 0
2 | CABLES :
2.1 | Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications.
2.1.1 | 3.5C x 120 Sq.mm. AL Cable- MAIN PANEL | R.M | RO |  |  | 0 | 0 | 0
2.1.2 | 3.5C x 95 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.3 | 3.5C x 70 Sq.mm. AL Cable | R.M | 80 |  |  | 0 | 0 | 0
2.1.4 | 3.5C x 50 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.5 | 3.5C x 35 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.6 | 3.5C x 25 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.7 | 4C x 16 Sq.mm. CU Cable - KPDB, BARDB & LPDB | R.M | 30 |  |  | 0 | 0 | 0
2.1.8 | 4C x 10 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.9 | 4C x 6 Sq.mm. CU Cable - KITCHEN EQUIPMENT | R.M | 20 |  |  | 0 | 0 | 0
2.1.10 | 4C x 4 Sq.mm. CU Cable - KITCHEN EXHUAST, FRESH AIR & AHU | R.M | 50 |  |  | 0 | 0 | 0
2.1.11 | 4C x 2.5 Sq.mm. CU XLPE Cable | R.M | 10 |  |  | 0 | 0 | 0
2.1.12 | 4C x 2.5 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.13 | 3C x 16 Sq.mm. CU able | R.M | RO |  |  | 0 | 0 | 0
2.1.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | R.M | 50 |  |  | 0 | 0 | 0
2.1.15 | 3C X 4sq.mm CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.16 | 3C x 2.5 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.17 | 3C X 4sq.mm CU PVC Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.18 | 3C X 1.5sq.mm CU PVC Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.19 | 1C x 70 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.1.20 | 1C x 4 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.1.21 | 2C X 2.5sq.mm CU Cable | R.M | 20 |  |  |  |  | 0
2.1.22 | 5C X 2.5sq.mm CU Cable - LCS | R.M | 20 |  |  |  |  | 0
2.2 | CABLE TERMINATION
Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
2.2.1 | 3.5C x 120 Sq.mm. AL Cable- MAIN PANEL | Nos. | RO |  |  | 0 | 0 | 0
2.2.2 | 3.5C x 95 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.3 | 3.5C x 70 Sq.mm. AL Cable | Nos. | 2 |  |  | 0 | 0 | 0
2.2.4 | 3.5C x 50 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.5 | 3.5C x 35 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.6 | 3.5C x 25 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.7 | 4C x 16 Sq.mm. CU Cable - KPDB, BARDB & LPDB | Nos. | 6 |  |  | 0 | 0 | 0
2.2.8 | 4C x 10 Sq.mm. CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.9 | 4C x 6 Sq.mm. CU Cable - KITCHEN EQUIPMENT | Nos. | 2 |  |  | 0 | 0 | 0
2.2.10 | 4C x 4 Sq.mm. CU Cable - KITCHEN EXHUAST, FRESH AIR & AHU | Nos. | 6 |  |  | 0 | 0 | 0
2.2.11 | 4C x 2.5 Sq.mm. CU XLPE Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.12 | 4C x 2.5 Sq.mm. CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.13 | 3C x 16 Sq.mm. CU able | Nos. | RO |  |  | 0 | 0 | 0
2.2.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | Nos. | 4 |  |  | 0 | 0 | 0
2.2.15 | 3C X 4sq.mm CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.16 | 3C x 2.5 Sq.mm. CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.17 | 3C X 4sq.mm CU PVC Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.18 | 3C X 1.5sq.mm CU PVC Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.19 | 1C x 70 Sq.mm, Copper, Flexible, Bunched together | Nos. | RO |  |  | 0 | 0 | 0
2.2.20 | 1C x 4 Sq.mm, Copper, Flexible, Bunched together | Nos. | RO |  |  | 0 | 0 | 0
2.2.21 | 2C X 2.5sq.mm CU Cable | Nos. | 5 |  |  | 0 | 0 | 0
2.2.22 | 5C X 2.5sq.mm CU Cable - LCS | Nos. | 4 |  |  | 0 | 0 | 0
| Sub Total of 2 |  |  |  |  | 0 | 0 | 0
3 | POINT WIRING :
3.1 | LIGHT POINT
Sub mains / Pre-Primary wiring i.e. from DB to room switch board shall be carried out for Pre-primary point using 2.5 sqmm copper stranded. All lighting fixture, wiring shall be carried out for primary point using 2.5 sqmm copper stranded & for secondary wiring 1.5sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduits" (including flexible conduits for drops to light fittings)". Individual junction / inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.
also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12-8 points/800 watts as per following configuration:(LDBs located at two locations as shown) (The Switch Socket cost shall be paid separately.)
From distribution board to switch board will be termed as Pre-primary point, average wiring length for Pre-primary point to be considered as 15 metres. From switch board to first light fitting and switch board to switch board will be termed as primary point, average wiring length for primary point to be considered as 6 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 4 metres. Light point wiring shall be included submains wiring from D.B. to room switch board.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.1.1 | Pre-Primary point (sub mains point) | Nos | RO |  |  | 0 | 0 | 0
3.1.2 | Primary point | Nos | 18 |  |  | 0 | 0 | 0
3.1.3 | Secondary Point | Nos | 60 |  |  | 0 | 0 | 0
3.2 | LIGHT POINT- for AUTOMATION
All lighting fixture, wiring shall be carried out for primary point using 1.5 sqmm copper stranded & for secondary wiring 1.5sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduits" & 1 pair 1.5sqmm jacketed cable in Separate Conduit (including flexible conduits for drops to light fittings)". Individual junction / inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.
From DB to first light fitting/driver will be termed as primary point, average wiring length for primary point to be considered as 20 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 5 metres. Light point wiring shall be included submains wiring from D.B. to room lights/Driver.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.2.1 | Primary point | Nos | RO |  |  | 0 | 0 | 0
3.2.2 | Secondary Point | Nos | RO |  |  | 0 | 0 | 0
3.3 | Power Point (Utility)
Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 2.5 sqmm copper stranded. Secondary wiring 2.5sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduit". Individual junction/inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.
From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 15 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 6 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.3.1 | Primary point | Mtr. | 96 |  |  | 0 | 0 | 0
3.3.2 | Secondary Point | Nos | 15 |  |  | 0 | 0 | 0
3.4 | Power Point (Kitchen & BAR)
Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 4 sqmm copper stranded. & Also used 3R x 2.5sqmm copper stranded. Secondary wiring 4 sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduit". Individual junction/inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.
From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 22 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 1 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.4.1 | Primary point | Nos | 31 |  |  | 0 | 0 | 0
3.4.2 | Secondary Point | Nos | RO |  |  | 0 | 0 | 0
3.5 | S & I of GI conduits including all accessories, clamps, spacers, bends, tee, cross etc. as required at site for miscellaneous use in following sizes:
3.5.1 | 20mm dia | Mtr | 50 |  |  | 0 | 0 | 0
3.5.2 | 25mm dia | Mtr | 180 |  |  | 0 | 0 | 0
3.6 | S & I of flexible GI conduits including all accessories, clamps, spacers, end adopters (Glands) etc. as required at site in following sizes:
3.6.1 | 20mm dia | Mtr | 50 |  |  | 0 | 0 | 0
3.6.2 | 25mm dia (COMMON) | Mtr | 120 |  |  | 0 | 0 | 0
3.7 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular shuttered type switch socket outlets with modular front plate, on Suitable MS box, G.I. back box and all required accessories etc. Supply & Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw / wall plugs and other necessary hardware, marking identification numbers of circuits & interconnections of the switch /sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND
3.7.1 | 5A X 2 ELECTRICAL SOCKET | Nos. | 10 |  |  | 0 | 0 | 0
3.7.2 | POS COUNTER | Nos. | 2 |  |  | 0 | 0 | 0
3.7.3 | 5A PLUG POINT | Nos. | 1 |  |  | 0 | 0 | 0
3.7.4 | 5/15A POWER PLUG POINT(MODULAR SWITCH & SOCKET) | Nos. | 36 |  |  | 0 | 0 | 0
3.7.5 | 20/32A METAL CLAD WITH 20A SP MCB & PLUG TOP | Nos. | 7 |  |  | 0 | 0 | 0
3.7.22 | 5 Pin Industrial Socket (3 PHASE) | Nos. | 2 |  |  | 0 | 0 | 0
3.7.24 | DATA POINT | Nos. | 12 |  |  | 0 | 0 | 0
| Sub Total of 3.0 |  |  |  |  | 0 | 0 | 0
4 | RACEWAYS, CABLE TRAYS & JUNCTION BOX
4.1 | S & I of GI trunking same as above but of size 100mm x 40mm x1.6 mm for power cables.(Electrical Room) | Mtr | RO |  |  | 0 | 0 | 0
(PROFAB/ASIAN/Approved equivalent)
4.2 | S & I of trunking same as above but of size 85mm x 38mm x1.6 mm thick for power/data cables. | Mtr | RO |  |  | 0 | 0 | 0
4.3 | S & I of trunking same as above but of size 65mm x 38mm x1.6 mm thick for power/data cables. | Mtr | RO |  |  | 0 | 0 | 0
(PROFAB/ASIAN/Approved equivalent)
4.4 | S & I of 1 Run x 25mm dia, GI Conduit in Floor. | Mtr | 80 |  |  | 0 | 0 | 0
4.5 | S & I of floor junction boxes similar to above but size 350mm x 350mm x 60 mm | Nos | RO |  |  | 0 | 0 | 0
4.6 | S & I of floor junction boxes similar to above but size 250mm x 250mm x 60 mm | Nos | RO |  |  | 0 | 0 | 0
4.7 | S & I of floor junction boxes similar to above but size 150mm x 150mm x 60 mm | Nos | 10 |  |  | 0 | 0 | 0
4.8 | S & I of GI Pregalvanizd Perforated type Cable Tay
of following sizes suspended from ceiling or fixed
vertically on wall/column as per route directed at site
including all necessary bends, tees, crosses and also
including all necessary supporting arrangement.
All supporting hardware including nuts, bolts etc.
shall be also of galvanised M.S. as approved
(PROFAB/INDIANA/ASIAN/approved equivalent)
4.8.1 | 100mm x 50mm x 1.6mm | Mtr | 10 |  |  | 0 | 0 | 0 | 1470
4.8.2 | 300mm x 50mm x 1.6mm | Mtr | 15 |  |  | 0 | 0 | 0 | 168
4.8.3 | 450mm x 50mm x 2.0mm | Mtr | RO |  |  | 0 | 0 | 0 | 90 | 375
150
| Sub Total of 4.0 |  |  |  |  | 0 | 0 | 0 |  | 420
5 | LIGHT FIXTURES INSTALLATION | [8 empty] | 210
5.1 | Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect / consultant at site.
5.1.1 | WALL LIGHT | Nos | 10 |  |  | 0 | 0 | 0
5.1.2 | LED STRIP LIGHT(Mtr.) | Mtr. | 65 |  |  | 0 | 0 | 0
5.1.3 | CEILING SPOT LIGHT | Nos | 40 |  |  | 0 | 0 | 0
5.1.4 | PENDANT LIGHT | Nos | 21 |  |  | 0 | 0 | 0
| Sub Total of 5.0 |  |  |  |  | 0 | 0 | 0
6 | EARTHING :
6.1 | S & I of earth pit comprising of specially designed SEE/Ashlok brand Earth Electrode system 3.00 meter long including necessary materials like side fill compound etc. as required with standard brick masonary chamber with hinged cover and watering arrangement model SEE-60/C with SFC-20/Equivalent ASHLOK MODEL T39 HD (50MM DIA. 3 MTR) | Nos | 2 |  |  | 0 | 0 | 0
6.2 | S & I of copper /GI earthing wires/strips in following sizes
6.3 | 8 SWG GI bare wire | Mtr | 90 |  |  | 0 | 0 | 0
6.4 | 8 SWG CU bare wire | Mtr | 30 |  |  | 0 | 0 | 0
6.5 | 25mm x 3mm thick GI strip welded & painted green | Mtr | RO |  |  | 0 | 0 | 0
6.6 | 25mm x 6mm thick GI strip welded & painted green | Mtr | 30 |  |  | 0 | 0 | 0
6.7 | S & I of isolated/dedicated earthing / grounding system for computers etc.using insulated green-yellow copper earthing wire laid/fixed bare on wall/ceiling from separately made earth pit to the equipment in following sizes The rate shall include termination also.
6.7.1 | 6 Sqmm copper, yellow-green/green insulation | Mtr | 20 |  |  | 0 | 0 | 0
6.8 | S & I of Main bus for isolated earth comprising of 300mm x 25 mm x 3mm thick Tinned copper bar fixed on insulated support and having 10 nos of holes and nut bolts studs for clamping the earth leads,all contained in MS/PVC box and having transparent acrylic cover as approved by the consultant | Nos | 1 |  |  | 0 | 0 | 0
| Sub Total of 6.0 |  |  |  |  | 0 | 0 | 0
7 | Miscellaneous Item
7.1 | Supply & Install. Of RG 6 TV Cable in 25mm GI Conduit | Mtr. | 30 |  |  | 0 | 0 | 0
7.2 | Supply & Laying of RG11 use for Main Cable TV | Mtr. | 50 |  |  | 0 | 0 | 0
7.3 | Install. Of Digital Screen - Only Installation | Nos. | 2 |  |  | 0 | 0 | 0
| Sub Total of 7.0 |  |  |  |  | 0 | 0 | 0
8 | DATA DISTRIBUTION
Supply, Installation, termination & testing of data system:
8.1 | Main SERVER / ROUTER | Nos. | 0 |  |  | 0 | 0 | 0
8.2 | SMART GIGABIT SWITCH 24 PORTS | Nos. | 0 |  |  | 0 | 0 | 0
8.3 | Loaded PATCH PANEL for 24Port | Nos. | 0 |  |  | 0 | 0 | 0
8.4 | LIU switch with Accessories. (Optional : if Fibre Optic Cable terminated) | Job | 0 |  |  | 0 | 0 | 0
8.5 | Supply & Installation of I/O DATA Outlet (RJ-45) | Nos. | 20 |  |  | 0 | 0 | 0
8.6 | S & I of Installation of Wi-Fi ceiling mounted Access Point, managed by controller software | Nos. | 0 |  |  | 0 | 0 | 0
8.7 | Supply, installation, termination & testing of all Terminations using Fluke Cable Analyser DTX 1800 for all CAT 6 Information Outlet including Information outlet | Lot | RO |  |  | 0 | 0 | 0
8.8 | CABLES:
8.8.1 | S&I Optical Fiber Cable with 12 fibers, with core dia. 50/125 µm (OM3), suitable for 1GBps Ethernet distance at 850 nm of wavelength, | Mtr. | RO |  |  | 0 | 0 | 0
8.8.2 | S&I Optical Fiber Cable with 6 fibers, with core dia. 50/125 µm (OM3), suitable for 1GBps Ethernet distance at 850 nm of wavelength, | Mtr. | RO |  |  | 0 | 0 | 0
8.8.3 | Supply & providing of CAT 6 UTP cables in the laid raceways/Conduits including terminations | Mtr. | 240 |  |  | 0 | 0 | 0
8.8.4 | Patch cord (2 mtr-user end) | Each | 20 |  |  | 0 | 0 | 0
8.9 | Supply, Installation, Testing & Commissioning of Velcro Ties ( 22 Mtrs = 1 Roll) | Roll | 0 |  |  | 0 | 0 | 0
8.10. | Supply, Installation, Testing & Commissioning of Cable Ties 200mm ( 100 Nos. Pkt) | Pkt. | 0 |  |  | 0 | 0 | 0
8.11 | Project Management including Freight & Forwarding, Cable Bunching, Printed Numbering, tube type Ferruling both sides, Face plate, Patch panel & patch cords both sides, Documentation etc.. | Job | 1 |  |  | 0 | 0 | 0
8.12 | Supplying and fixing 15U Rack Aluminium Frame - 600x600mm with 4 x FAN, Dual Split perforated Door at Front and Back Side, 2 x Vertical Cable Basket, 2 x 12 socket 5/15A PDU with MCB, side Panels of 2 nos and Heavy Duty Castors with break, 19" Reduced Channel - Loop Type (DATA+CCTV) | Job | 0 |  |  | 0 | 0 | 0
8.13 | Supply & installation of GI Conduits with junction boxes, reducer etc. complete concealed/surface mounting as required.
| Sub Total of 8.0 |  |  |  |  | 0 | 0 | 0
9 | SUPPLY & INSTALLATION OF SAFETY ITEMS
9.1 | Sand buckets with stand (set of 3 buckets) | Sets | RO |  |  | 0 | 0 | 0
9.2 | Caution boards (11kV) of standard Size | Nos | RO |  |  | 0 | 0 | 0
9.3 | Caution boards (415V) of std. Size | Nos | 1 |  |  | 0 | 0 | 0
9.4 | Rubber mat at panel room 12mm thk. 1mtr. Wide | Mtrs | 1 |  |  | 0 | 0 | 0
9.5 | Shock treatment chart as per electricity board | Nos | 1 |  |  | 0 | 0 | 0
9.6 | First aid box with standard items | Nos | RO |  |  | 0 | 0 | 0
9.7 | 11 KV rating rubber hand gloves | Sets | RO |  |  | 0 | 0 | 0
9.8 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical & ELV Services executed at site. | Part of Tender |  |  |  | 0 | 0 | 0
| Sub Total of 9.0 |  |  |  |  | 0 | 0 | 0
10 | UPS/ INVERTER System:
10.1 | Supply, Installation, testing and commissioning of 3 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. Make: Emerson/APC/Consul Neowatt/Vivtar Electronics | set | 1 |  |  | 0 | 0 | 0
| Sub Total of 10 |  |  |  |  | 0 | 0 | 0
11 | CCTV
11.1 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Dome + Night vision. Camera Make: CP-PLUS | Nos. | 0 |  |  | 0 | 0 | 0
11.2 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Bullet Camera+ Night vision. Camera Make: CP-PLUS | Nos. | RO |  |  | 0 | 0 | 0
11.3 | Supply & Installation of 2 Megapixel IR-30Mtr. IP Outdoor Bullet Camera + Night vision. Camera Make: CP-PLUS | Nos. | RO |  |  | 0 | 0 | 0
11.4 | Supply & Installation of 16 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | 0 |  |  | 0 | 0 | 0
11.5 | Supply & Installation of 24 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | RO |  |  | 0 | 0 | 0
11.6 | Supply & Installation of 16 Channel NVR with 2 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | 1 |  |  | 0 | 0 | 0
11.7 | Supply & Installation of 16Port PoE Switch (Make: Systimax) | Nos. | 1 |  |  | 0 | 0 | 0
11.8 | 6 TB HDD Hard Disk | Nos. | 2 |  |  | 0 | 0 | 0
11.9 | Monitor/PC system | Nos. | 2 |  |  | 0 | 0 | 0
11.1 | Supply & Installation of 3+1 Cable for Camera Signal | Mtr. | 150 |  |  | 0 | 0 | 0
| Sub Total of 11 |  |  |  |  | 0 | 0 | 0
12 | PA SYSTEM
12.1 | Supply & Installation of 6W Ceiling Speaker with box | RM | 6 |  |  | 0 | 0 | 0
12.2 | Control Unit (with volume and on/off switch) (Smooth stepless control, but the control shall be through dimmer switch, the make of which will be same as the make of light control switches) | Nos. | 1 |  |  |  |  | 0
12.3 | Supply & Installation of 120W Booster Amplifier | Nos. | 1 |  |  | 0 | 0 | 0
12.4 | Installation of 2 core 2.5 Sq.mm PVC insulated twisted copper conductor Speaker wires as required. | RM | 60 |  |  | 0 | 0 | 0
| Sub Total of 12 |  |  |  |  | 0 | 0 | 0
General guideline for onsite electrical works:
1. DB have per phase RCBO protection.
2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.
3. All equipment’s above 1 KW shall be provided with ELCB & shall run/operated through industrial type switch socket only.
4. Only GI conduit will be used.
5. Equipment protection devices and appropriate earthing as per approved load to be provided.
6. All DB and panel have dual earthing connection.
7. All internal wires / cables shall be FRLSH/FRLSZH.
8. Main distribution board will not be fixed on wooden material.
9. IT , Data and low voltage wires shall be drawn In Separate
10. Switch/ Sockets outlets will not be over loaded with multiple connection conduit and not with electrical
11. All lights shall be LED.
12. Provision of Emergency light should be there.
13. No combustive material are to be store under/closed the electrical switch board/distribution board/meter etc.
14. The concessioner should install suitable type & rated fire extinguisher near electrical panel.
15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.
16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.
17. Final approved Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.
18. Load balancing to be done.
19. Power connection for Existing BTU meter & Water meter to be provided from concessionaire DB.
20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.
21. Panel GA drawing to be share with DIAL for approval.
22. Before installation, material inspection to be done.
23. Test certificate for installed electrical material to be submitted to DIAL .
24. If any changes due to site constraint, prior intimation to be provided to DIAL. Post approval only SLD to revised.
In case, Incomer rating equal to or more than 200Amps: Automatic Tube Detection and Suppression System to be done
CO2,FM200/HFC-227ea gas based automatic tube detection & suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.
Drawing needs to be submitted for prior approval.
System sizing & design calculations also need to be incorporated in drawing.