## FAS
BILL OF QUANTITY FOR ELECTRICAL WORK FOR IRRISH HOUSE @ DELHI
TENDER BOQ. R0
SR. | DESCRIPTION OF ITEM | UNIT | QTY | UNIT RATE (Rs.) |  | AMOUNT (Rs.)
NO. |  |  |  | MAT. | INST. | MAT. | INST. | TOTAL
13 | FIRE ALARM SYSTEM
13.1 | Single Loop Analog Addressable Fire Alarm Control panel (Expandable upto 1 Loop) with battery back up for 4 hours normal operation and 15 minutes alarm operation. The control panel per Loop Capacity 250 Detectrs and Devices, battery charger etc., 8.5" Touch Screen LCD Display, TCP/IP Connectivity, 10000 Event Log, Keyless Log on Using RFID Cards. The panel shall be UL listed and preferably FM approved with response time less than 10sec. Installation of fire alarm system shall be done as per IS 2189 or relevant NFPA standard.The panel shall have the web enabled facility which can able to send or receive e-mails with memory of 1000 events recording.Note:The vendor shall provide panel UL 9th edition listing certificate. (Make: Edwards / Honeywell) | Nos | RO |  |  | 0 | 0 | 0
i) Each loop with Min. 99 Devices + 99 Detectors modules connection capability of Addressable FACP) 2 Loop Pannel.
ii) FACP with all in-built modules & displays.
iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 4 hours normal working.
iv) Programming & setting up
v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station.
vi) As the number of hooters are 43, additional power supplies to be provided as required.
Necessary Integration Facility with BMS for following functions:-
Alarm, Trouble condition,Supervisory alerts to BMS
Share Graphics of Security, Fire and HVAC
13.1.1 | Fire alarm Addressable control panel (1 Loop)
13.2 | Active Repeater Panel with 8.5" Touch Screen TFT display with TCP/IP Eable Repeater Panel shall monitor and control (Scroll, Acknowledge, Reset & Mute) all the events of the FACP to which it is connected and it shall have Port Vectoring / Event Filtering capability of showing only ALARMS, TROUBLES or SUPERVISORY or customized combinations of user selected events. | Nos | 1 |  |  | 0 | 0 | 0
13.2.1 | Supply installation and testing of signal loop components in a suitable galvanised steel junction box.
13.3 | Detectors and Devices
13.3.1 | Supply,Installation,Testing & Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices & shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Nos | 2 |  |  | 0 | 0 | 0
13.3.2 | Supply,Installation,Testing & Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system for AHU tripping and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Nos | 1 |  |  | 0 | 0 | 0
(For all AHU's, Fans & Acess Control)
13.3.3 | Supply,Installation,Testing & Commissioning of Horn / Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with Control modules and necessary accessories including back box. | Nos | 2 |  |  | 0 | 0 | 0
13.3.4 | Supply, Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors( Below False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | RO |  |  | 0 | 0 | 0
13.3.5 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric smoke detectors (Above False Ceiling) having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | RO |  |  | 0 | 0 | 0
13.3.6 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Photoelectric Multi Sensor detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-SIGA PHD) | Nos | 8 |  |  | 0 | 0 | 0
13.3.7 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type Heat Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Nos | 2 |  |  | 0 | 0 | 0
13.3.8 | Supply,Installation,Testing & Commissioning of Analogue Addressable Flash scan Type GAS leak Detector having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. (Make- Edward-EST-SIGA-HFS) | Nos | RO |  |  | 0 | 0 | 0
13.3.9 | Supply,Installation,Testing & Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressable module that monitors and reports contact status. | Nos | 2 |  |  | 0 | 0 | 0
13.4 | SITC of Fault Isolator. | Nos | 1 |  |  | 0 | 0 | 0
13.5 | SITC of 2Cx1.5sq.mm multistranded FRLS Cu. Armoured for RED Colour,Mylan Shielded Screened cable For SLC. | Mtrs | 120 |  |  | 0 | 0 | 0
13.6 | Response indicator. | Nos | RO |  |  | 0 | 0 | 0
| Sub Total of 13 |  |  |  | 0 | 0 | 0 | 0