## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  |  | Provisional Sum
B | HVAC EQUIPMENTS - AC EQUIPMENT (CHILLED WATER - TYPE) Supply, installation, testing and commissioning of chilled water type High static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3/G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping. The unit shall be suitable for 230 ± 10 volts, 50/60 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level. (Make: Waves, System Air, Daikin, Voltas, Caryaire,Blue Star or equivalent with airport approval)
B1.1 | 5.5 TR - (2200 CFM @ 90-100 PASCAL -ESP) | Nos | 1
B.2 | AIR CLEANING EQUIPMENTS - Supply, installation, testing and commissioning of Double Skinned ceiling suspended Electrostatic Precipitator(ESP) of approved make with minimum 25 mm thick panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50/60 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. (Make: Rydair, Trion or equivalent with airport approval)
B.2.1 | 3600 CFM | Nos | 1