## LMS BOQ
Project: Blue Sea Banquet Hall
SI.No | DESCRIPTION | Item Image | Location | LL- Mezzanine | LL-Ground | TOTAL QTY. | UNIT | SUPPLY |  | Installation
[8 empty] | Rate | Amount | Rate | Amount
1 | Part A - LIGHTING MANAGEMENT SYSTEM - LMS
1.1 | Supply, Installation, Testing & Commissioning of Wireless personlised control Keypad with a WPC approved frequency of 865 Mhz, 4 Buttons for scene selection, with faceplate,mounts on glass surfaces also, with 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required similar to Lutron PN2-4B-TAW-L31 + LPFP S1 TAW |  | Wall Mounted | 1 | 2 | 3 | Nos. |  | 0 |  | 0
1.2 | Supply, Installation, Testing & Commissioning of Wireless personlised control Keypad with a WPC approved frequency of 865 Mhz, 2 Buttons for On/Off selection, with faceplate,mounts on glass surfaces also, with 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required similar to Lutron PN2-2B-TAW-L01 + LPFP S1 TAW |  | Wall Mounted | 1 | 3 | 1 | Nos. |  | 0 |  | 0
1.3 | Supply, Installation, Testing & Commissioning of QS Sensor Module, to connect 10 number of sensors either of the Occupancy / Daylight / Personal sensors/PIco. No wired connections, ceiling mount Similar to QSM5-XW-C |  | Ceiling mount | 2 | 1 | 3 | Nos. |  | 0 |  | 0
1.4 | Supply, Installation, Testing & Commissioning of DALI Dimming controller; Controls 2 independent DALI links with up to 64 DALI ballasts per link. Can take care of Color Tunable fixtures. 4 groups of sensors inputs: Occ sensor, daylight sensor and IR sensor. Requires mains/line voltage feed Similar to Lutron QSN-2DALUNV-D |  | Electrical Room within DB | 1 | 1 | 3 | Nos. |  | 0 |  | 0
1.5 | Supply, Installation, Testing & Commissioning of Switching module with 4 channels, each channel with minium 5 amp rating with provisions of sensors inputs: Occ sensor, daylight sensor and IR sensor. Requires mains/line voltage feed Similar to Lutron QSNE-4S 5230D module |  | Electrical Room within DB/ Or nearest closests | 1 | 2 | 1 | Nos. |  | 0 |  | 0
1.6 | Supply, Installation, Testing & Commissioning of International seeTouch QS Wallstation Insert 5-10 Button with Raise/Lower QSWE-10BRLN-AW |  | Wall Mounted | 1 | 0 | 1 | Nos. |  | 0 |  | 0
1.7 | Supply, Installation, Testing & Commissioning of central processor assembled processor with two configurable links. Each processor link can be configured to be a dimmer link, shade link, or dimmer power panel link. Processor accpets 220-240V, 1 phase, 2 wire, 10A feed, (throiugh power supply) Similar to Lutron Athena |  | Electrical Room within DB/ Or nearest closests | 1 |  | 1 | Nos. |  | 0 |  | 0
1.8 | Supply, Installation, Testing & Commissioning of Power Supply Unit for supply PDUs to Antenna devices Similar to Lutron QSPS-DH -1 -75 |  | Electrical Room within DB/ Or nearest closests | 1 |  | 1 | Nos. |  | 0 |  | 0
1.9 | Supply of QS cable for power and data simialr to Lutron QS‐CBL‐LSZH Cable Adheres to CE standards for Low Smoke Generation (EN 60332‐1‐2), Halogen Gas Emission (EN 61034‐2), and Flame Retardation (EN 60754‐1&2). • Five Conductors: Common – 0.75 mm2 (18 AWG) Power – 0.75 mm2 (18 AWG) MUX Data – 0.25 mm2 (22 AWG) _ Data – 0.25 mm2 (22 AWG) Drain Wire – 0.2 mm2 (24 AWG) Supply & Laying of suitable conduits to be done by Electrical contractor. |  | QSMs and DB Box | 140 | 130 | 250 | Meters |  | 0 | Electrical contractor scope
1.1 | DB BOX for mounting dimming , swithcing module |  | Electrical room | 1 | 1 | 1 | Nos. |  | 0 |  | 0
1.11 | DALI flexible cable 2C X 1.5 Sqmm for loop in loop out. |  |  |  |  | 0 | Meters | Electrical contractor scope |  | Electrical contractor scope
1.12 | Complete commissioning of the system |  |  |  |  | 0 | Lot |  |  | 80000 | 0
| Total for Part A - LIGHTING MANAGEMENT SYSTEM - LMS | [7 empty] | 0 |  | 0

## TOC (hidden)
<<toc¦gmtOffset:GMT+05:30>> | [6 empty] | Event: | Tender for Electrical - 2019 (Vikhroli Godrej 2) | <<system>> | pcdos | <<paletteLock>> | -16777216,-8355712,-2500135,-4144960,-1,-5855578,-7155632,-52,-2167817,-3092786,-65536
TOC | N1 | [5 empty] | EventNumber: | 4527 | <<release>> | 16.0
TOC | N2 | [5 empty] | Phase: | RFP | <<osversion>> | Windows (64-bit) NT :.00
TOC | P1 | [5 empty] | Task: | RFP
Summary | B1 | [5 empty] | Downloaded By: | Amit Parkar
TOC | N3 | [5 empty] | Download time: | Jan 6, 2020, 5:54:40 PM GMT+05:30
TOC | E15 | [5 empty] | Company: | Turnkey
TOC | E20 | [5 empty] | Role: | Supplier
TOC | E25
TOC | E30
TOC | E35
TOC | E40
TOC | E45
<<end>>
|  | <<decimalSeparatorFormula>> | .
|  | <<event>> | 9219603401988134523,Tender for Electrical - 2019 (Vikhroli Godrej 2)
|  | <<template>> | 5.+MAERSK-EL-BOQ.xlsx
|  | <<tId>> | 9219604425040982929
|  | <<task>> | 9219604424113361777
|  | <<company>> | Turnkey
|  | <<structure¦id:5.8>> | <<sheethash>> | <<sheethash>> | <<sheetpwdhash>> | <<end>>
|  | <<define>> | 375601 | -2800197691211 | 49561
|  | <<define>> | 371601 | -1929872582100 | 49561
|  | <<define>> | 372610 | 12592833402110 | 49561
|  | <<define>> | 370610 | 16234724051201 | 49561
|  | <<define>> | 374611 | 832402111 | 49561
|  | <<define>> | 373610 | 21067281311200 | 49561
<<end>>