## HIGH SIDE
NAME OF PROJECT: BUDWEISER BAR AT MOPA GOA
HVAC WORK (HIGH SIDE)
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
A | EQUIPMENTS |  |  | RATE |  | AMOUNT
1 | KITCHEN EXHAUST AIR SCRUBBER
Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications.
Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type SS Filters with aluminium mesh filters, Tungsten wire type type ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area, collection area should not be less than 6.0 sqmt, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state and entier unit should be CE Certified. all units shall have shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety. The units should be BMS compatible for Feedback information on Run,Wash and Fault,dry contact point. The system should allow connection to a fan section to achieve velocity between 2.5 - 3.8 m/s across the air cleaner and should units should meet MERV 15 requirements even at velocity of 3.81 m/s (750 FPM)
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
ESP Power Consumption : Not more than 50W per cell.
Air Moving Capacities are as follows:
| 4700 CFM | No. | 1
2 | FAN COIL UNITS
Supplying, installing, testing and commissioning of horizontal powder coated Medium Static Chilled Water Fan Coil Units, blow thru type, Noscomplete with 3/4 rows deep chilled water coil, one or more centrifugal fans, aluminum/synthetic cleanable pre-filters,Digital thermostat with necessary control and power wiring with PVC conduit etc. type , primary inside pan SS-304 & secondary condensate drain pans outside of GI duly insulated, casing, coil, piping connections through copper pipes, condensate drain connection, All fan coil units shall be suitable for 220±6% volts, 50 cycles single phase power supply. All fan coils shall be with factory fitted with complete valve station, 2 way PIBC chilled water valve along with On -off type 220/230 volt AC actuator , brass made Y strainer type ball valve, brass ball valve.All valves shall be of minimum PN-16 pressure rating Quoted rates shall be inclusive of the cost of valve's thermal insulation (CFC & HCFC free) as specified for chilled water piping thermal insulation, 2 way PIBC Motorized Valves provided with spring return function in chilled water lines at Nosfan coil unit. The valves shall be suitable for suitable pipe sizes. 2 way PIBC control valve chilled water valve will be of PN16 rating complete with motor 220/230 volt AC of actuator of suitable torque.The valve should be IEC 534 compliant , have 20 mm stroke All shall be supplied as per tender specifications and data sheet. Fan coil unit shall be of following arrangement and refrigeration capacity.Control wiring from thermosets to FCU motor & PICV valve unto 20 Mtr. length shall be inclusive. 3C x 1.5 Sq.mm.Power cable of 3 mtr.length with 3 pin plug top from unit motor to the nearest power socket shall be included in the scope of supply.All supporting GI hangers, ,MS angles, channels nut , bolts, washers etc. necessary for unit installation shall be inclusive in the cost. Unit should supply with necessary Corded Remote Controller.
| 2.5 TR ( 1000 cfm) | Nos. | 1
3 | Ceiling Suspended AHU
Supplying, installing, testing and commissioning of double skin construction draw thru type Ceiling Suspended AIR HANDLING UNITS as per specification, each complete with ESP Filter (94% down to 3 microns), pre-filter section (90% down to 10 microns), min 6 Row Deep Chilled water coil of copper tube & aluminium fins construction, squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (IE2) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3.All units shall be complete with opposed blade volume control dampers at oulet. Duct flexible connector (fire proof) shall be provided at outlets of AHU. ( Temporary bypass arrangement in Chilled Water Line with related accessories to be considered to facilitate flushing during precommissioning and commissioning of the System).
AHU Tag. Description AHU CFM TR ESP Motor HP
| AHU-01 Sitting area 3000 cfm 6 15 mm 2 | No. | 1
4 | Supplying, installing, testing and commissioning of AIR HANDLING UNITS ( FAN SECTIONS ONLY)with double skin construction as per specificatopns, each complete with squirrel cage induction motor (mounted internally), airfoil centrifugal fan belt drive and vibrations isolators.Motors shall be suitable for 415 +- 10% volts, 50 cycles , 3 phase AC supply an static pressure shall be as indicated . Fan-motor assembly (as whole) shall be statically & dynamically balanced to grade G6.3 as per ISO-1940/AMCA 204-3. AHUS (Fan sections) shall be complete with duct flexible connections and volume control damper . In additional all supply fans (SF) shall be provided with prefilter
SF - Supply Fan
Sr.no Fan Tag Space Fed CFM SP Motor HP (mmwg)
| 1 SF -01 Kitchen 4250 40 3 | No. | 1
5 | Supply, installation, testing and commissioning of single width single inlet class I centrifugal fans for ventilation system. Each fan shall be complete with totally enclosed fan cooled motor, belt drive, pulley mounted on motor & fan shaft, belt guard, motor mount and vibration isolators. The motor shall be suitable for 415 V + 10% volts 3 phase 50 cycles, AC supply & suitable for operating through VFD. The motor selected shall be energy efficient having efficiency at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. The fan shall be low RPM and capacities based on 2.5 inch (6.5 cm WC) static pressure. Fan capacities shall be as follows:
EF - Exhaust Fan
Sr.no Fan Tag Space Fed CFM SP Motor HP (mmwg)
| 1 EF -01 Kitchen 4700 65 5 | No. | 1
6 | Ductable Split unit
Supply, installation, testing and commissioning of CONCEALED Duct type units with Scroll compressor with green Regrigerant R-410A/R-32/R-22. The unit should be complete with indoor & outdoor unit, condensing unit, controls, control panel, tubular type refrigerant, canvas connection remote control and drain piping. The refrigerant piping, control wiring should be based on the indoor unit and outdoor unit distance being 3 mtrs/Ckt along with 13 mm thk nitrile rubber insulation. The insulated drain piping should be of 32 mm dia. and distance 3 mtrs/unit. Indoor unit should be provided with thermostats and remote control. The installation should be complete with all the required accessories like the supports, clamps required to make the installation complete. The cost should also include Chasing in walls as well as all the supports needed to install the units at the higher level.
The quoted price shall include the GI frame structure to mount the outdoor unit or to suit the site condition.
6.1 | 8.5 TR ( 3400 cfm) HSP split air conditioning units as described above | No. | 1
TOTAL
GRAND TOTAL (SUPPLY + INSTALLATION)

## LOW SIDE
NAME OF PROJECT: BUDWEISER BAR AT MOPA GOA
HVAC WORK(LOW SIDE)
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
A | EQUIPMENTS
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 18 G sheet | sq.m | 30
| 20G sheet | sq.m | 5
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 110
| 26G sheet | sq.m | 5
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 18 G sheet | sq.m | 5
| 20G sheet | sq.m | 5
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 5
3 | THERMAL INSULATION FOR KITCHEN DUCTS
SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade.
| 80 mm Thick | sq.m | 30
4 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 3
5 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 0.5
6 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape supply air diffusers with removable core & anti smudge ring & volume control dampers as per approved drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | Nos. | 1
7 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction. Square / round shape return air diffusers with removable core, antismudge ring & without volume control damper as per specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 1.5
8 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 5
9 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Return air Grilles without volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 4
10 | Supply, installation and testing of Acoustic lining with Open cell nitrile rubber with in supply and return air ducts of specified thickness as per the specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as perthe specifications:
| 15 mm thick | sq.m | 20
11 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber(Class“O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
| 19mm thick | sq.m | 75
12 | Supplying, installing and testing of UPVC pipe ( heavy duty) with 6 mm thick nitrile rubber insulation with protective coating on condensing water piping and fitting like bends, elbow, tee and union, etc. as per the approved shop drawings and specifications.
| 32 mm Dia | Rmt | 10
| 25mm Dia | Rmt | 5
13 | Supply ,Installation ,Testing and commissioning of ERW heavy duty C Class MS pipes as per IS-1239 upto 6" dia. and as per IS-3589 above 6" dia. cut to required lengths and installed with all welded joints, complete with necessary pipe hot dip galvanized MS supports, GI hangers with rubber lined universal clamps and hangers , fittings like bends, elbows, tees, reducers, matching flanges, neoprene 6 mm thick gaskets, hot dipped galvanized nut & blots & washers ,PUF gutti with U clamp, socket and fittings for instruments and sensors connections etc. ERW pipes shall be with two coats of Zinc Chromate paint for anti-rust including all fittings like valves, flanges and unions, etc. Note : Pipe Measurement are in Pair (Supply + Return) . Quoted rates shall be inclusive of the cost of piping Insulation of Class O rated thermal insulations with one sided factory laminated glass clothed Nitrile Rubber insulation with density 45-60 kg/m3 with covered with two coats of UL Listed lag coating (Low VOC) Anti-fungal, Anti-microbial & vapour barrier for line item sealed with acrylic based food grade sealant.
| 25 mm dia MS Pipe with 25 mm thick Insulation | Rmt | 10
| 32 mm dia MS Pipe with 25 mm thick Insulation | Rmt | 5
| 40 mm dia MS Pipe with 25 mm thick Insulation | Rmt | 5
14 | Providing and fixing in position following ball valves
14.1 | 25 mm dia valves | Nos. | 1
14.2 | 32 mm dia valves | Nos. | 2
14.3 | 40 mm dia valves | Nos. | 3
15 | Providing and fixing in position the following ball valves with Y-strainer (PN 16).
15.1 | 25 mm dia valves | Nos. | 1
16 | Providing and fixing in position the following ‘Y’ Strainers :
16.1 | 40 mm dia strainers | Nos. | 1
17 | Supplying, installation, testing and commissioning of Auto air vents.
17.1 | 25 mm dia pipes | Nos. | 2
18 | Providing and fixing in position SS 304 the industrial dial type pressure gauges with gun metal valves. | Nos. | 2
19 | Providing and fixing in position SS 304 the mercury-in- glass industrial dial type thermometers. | Nos. | 2
20 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display & fan speed control, capable of providing individual space temperature control for cooling application. The controller shall produce a dual output to cooling coils in response to load change in rooms. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water duty . (minimum of 5 Deg F dead band ) | No. | 2
21 | Supply, installation, testing and commissioning of Electronic Self Balancing Valve pressure independent with independent type dynamic balancing valve for AHUs with integrated 2 way modulating control valves in a single body. The actuator shall be capable of accepting 2-10 VDC / 4-20 mA electric signal and shall provide similar transduced feedback output signal to control system for flow measurement. The minimum close off pressure actuator must be 1.5 times shut off head of pump 5 bars whichever is maximum. The valves shall be suitable for following pipe sizes:
21.1 | 32 mm dia | No. | 1
21.2 | 25 mm dia | No. | 2
22 | Supply, Installation, Testing and Commissioning of BMS compatible ultrasonic BTU Meter complete with flanged type water flow meter (pressure drop across water meter not exceeding 0.1 bar at the specified nominal flow rate), temperature sensors, LCD display panel, inbuilt Lithium battery backup with minimum six years life. The units shall be capable to calculate and store maximum values, display flow rates and temperature difference across supply and return. The quoted price shall be inclusive of necessary wiring, conduiting between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box. The size of the BTU meter is as under:
22.1 | 40 mm dia BTU Meter | No. | 1
23 | Providing & fixing of inter connecting copper piping between indoor & outdoor units as per manufacturer specifications duly insulated with closed cell nitrile foam tabular insulation of 13mm thickness. All piping inside the room shall be properly supported with hanger in M.S. painted cable tray and exposed piping shall be properly supported in G.I. cable tray with top cover
23.1 | 15.9 mm OD soft copper (Insulation 13 mm) | RM | 15
23.2 | 28.6 mm OD soft copper (Insulation 13 mm) | RM | 15
24 | Supply, laying, testing and commissioning of PVC sheathed stranded FRLS wires in MS conduits recessed / surface including cutting, chesing the wall surface and making for the same, sizes as given below of copper conductor including terminations complete as required.
24.1 | 2C x 1.5 mm2 (control wiring for IDU to ODU) | RM | 20
25 | CONTROL PANEL FOR AHU & FAN (WITH DOL / SD STARTER)
Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing & terminating into MCCB in each panel shall be provided by the electrical contractor.
All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included.
All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System.
The panel shall include the following components and accessories.
a. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA.
b. | DOL / SD starter as per HP ratings
c. | Terminal block for power distribution.
d. | Contactor, over load relay with built in single phasing protection.
e. | Phase indicating lights and indicating light for ON status.
f. | Digital voltmeter and digital ammeter with selector switches.
g. | Time delay relay for delayed automatic restart of air handling unit motor.
h | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
i | All starters shall be provided with suitable potential free contract for connections to the Building Automation System.
The number of AHU/ FAN control panels shall be as follows.
| Up to 5 HP DOL Starter | No. | 3
GRAND TOTAL

## MAKE LIST
NAME OF PROJECT: BUDWEISER BAR AT MOPA GOA
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Thermal Insulation on Kitchen Duct | UP Twiga, Owens Corning, Supreme
9 | Dry Scrubber | Rydaire / Trion / Halton
10 | Fan coil unit / Air Handling Unit | Zeco/ Edgetech / Carrier/ Blue star / Waves
11 | M.S. Pipe upto 200 MM Dia. | AST / Jindal Hissar / Prakash Surya /Tata Steel
12 | UPVC Drain Piping | Prince / Supreme
13 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
14 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
15 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
16 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
17 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
18 | Cables | Polycab / Finolex / Hawells
19 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
20 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
21 | ESP Filter | Honeywell/Magneto/Trion
22 | Ball valve | Honeywell/Zoloto/Emerald /Advance Valve /Navtech (Castle
23 | Y Strainer | Emerald / Rapidcool
24 | Pressure Gauge | Emerald /Fiebig /H Guru
25 | Thermometer | Emerald /Fiebig /H Guru
26 | Auto Air Vent Valve | RB / Rapid Control
27 | PIBCV for AHU | Belimo / Danfoss / Honeywell / Schneider / Siemens
28 | Room Thermostat | Danfoss / Honeywell / Schneider / Siemens
29 | Starter | Siemens / Allen Bradley/ ABB / Schneider / L & T
30 | BTU Meter | Johnson Control / Honeywell / Kamstrup / Landis Gyr
31 | SISW FAN / AHU FAN Section | Airflow / Kruger / Nicotra/ Systemair
32 | Split unit | Toshiba / Bluestar / Daikin / Samsung / Mitsubishi/LG/Hitachi /Voltas