## SUMMARY
AJ KITCHEN @ T1, AHMEDABAD AIRPORT
HVAC BOQ SUMMARY
Sr.No | Description | Total Amount
1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) : | 250000
2 | CHILLED WATER PIPING WITH INSULATION: | 134900
3 | VENTILATION SYSTEM | 200000
4 | SHEET METAL WORKS: | 267750
5 | THERMAL & ACOUSTIC INSULATION: | 120250
6 | ELECTRICAL WORKS: | 76000
| SUB - TOTAL WITHOUT TAX | 1048900
| CGST @ 9% | 94401
| SGST @ 9% | 94401
Other taxes if applicable
| TOTAL WITH TAX | 1237702

## HVAC
AJ KITCHEN @ T1, AHMEDABAD AIRPORT
HVAC BOQ
Sr. No. | Description Items | Unit | Qty | Supply Rate | Installation Rate | Total Amount
Sr.No. | Item Description
Note: | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) :
1.1 | CEILING SUSPENDED AHU :
Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications:
Frame Structure: It shall consist of 48mm Extruded Aluminium with thermal break profile.
Panel: 45mm +/- 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg/m3 or PUF insulation of 48 kg/m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI.
Filtration Section: It shall be provided with single stage washable type of prefilter 'MERV 8' first stage which shall be placed before coil section.
Coil Section: Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m/sec (500 fpm).
Drain Pan: Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation.
Fan Section: SISW / DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration.
Other Details : AHU to house control box/ terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over/ Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers / Fire Alarm Panel. Power cable from Terminal box to motor & control cabling of required size upto the thermostat / sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports & accessories required for installation.
Contractor shall design the chilled water coil according to the following conditions:
a. Coil air entering temperature - 75.4°F DB
b. Coil air leaving temperature - 54 deg. F DB/ 52.99 deg. F WB
c. Chilled water temperature entering - 6.0 deg. C/ 42.8 deg. F
d. Chilled water temperature leaving - 13.3 deg. C/ 55.9 deg. F
Make : VTS / Zeco / Citizen
Type Capacity Tonnage ESP No. of
(Cfm) TR (mm WG) Rows
a | CS AHU 1500 4.32 25 4/6 | No. | 1 | 230000 | 20000 | 250000
GENERAL NOTES:
a. | LHS & RHS VALVE station location to be confirmed.
b. | Fan outlet velocity - 1600 FPM
c. | Contractor shall submit static pressure calculation for all above units to Client/Consultant.
d. | Any change in motor HP shall be made at no extra cost to client.
e. | Fan efficiency shall be minimum 75%
f. | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
| SUB-TOTAL |  |  |  |  | 250000
2 | CHILLED WATER PIPING WITH INSULATION:
2.1 | CHW PIPE
SITC of MS Heavy duty class 'C' ERW Chilled Water pipe conforming to IS 1239 - 2004 primer painted including bends, tees, MS supports, PUFF saddles, anchor fasteners, steel angles and any other material required to complete the work. The piping flange connection bolts, washers and nuts should be hot dipped galvanised. Flourscent Plastic Sticker/ paint shall be applied to indicate Water flow directions. Only End flanges to be used for capping of pipes. "Table E" of BS code for flange thickness to be adhered.
Make: Jindal Hissar / TATA
a | Φ 32 mm | Rmt | 20 | 1350 | 200 | 31000
2.2 | CHILLED WATER PIPING INSULATION - INTERNAL USE
SITC of insulation for chilled water. piping. For internal pipe - Stick 25mm thick Nitrile rubber class "O" Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape and putting PVC bands at all supports.
Make: Armaflex & K-flex
a | Φ 32 mm | Rmt | 20 | 420 | 90 | 10200
2.3 | BALL VALVE
SITC of following sizes of Ball Valve consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Same valve shall be used as a Drain valve.
Make: Zoloto / Audco / Kitz
a | Φ 32 mm | Nos. | 3 | 4500 | 500 | 15000
2.4 | BALL VALVE WITH Y-STRAINER
SITC of following sizes of Brass Ball Valve with Y-Strainer consist of Cap, Brass Body, Rated for 150 psi SWP, 600 psi WOG Pressure: Two-piece construction; with brass body, regular port, B-16 chrome-plated ball and stem, replaceable “Teflon” or “TFE” seats and seals, blowout-proof stem, vinyl covered steel handle, threaded or soldered ends and extended stem for insulated piping. Filter element shall be of non magnetic SS sheet with perforation.
Make: Zoloto / Audco / Kitz
a | Φ 32 mm | No. | 1 | 12500 | 1000 | 13500
2.5 | PIBCV VALVES
SITC of Pressure Independent Balancing cum Control Valves (PIBCV) including integrated motorised control valve and balancing device for combined flow and water balancing requirement. Valve body to be rated for PN 16. The valve design flow rate should be factory calibrated with +/- 5% flow accuracy. Valve shall have necessary measuring ports, drain port, flanges etc., Valve shall also provide temperature sensor with necessary cabling (min 2mtr length to be considered with each valve). The balancing to be done through microprocessor based hand held terminal / POT and the same results shall be furnished in the water balancing report as part of commissioning report and handing over manual.
Make: Oventrop / Siemens / Danfoss
a | Φ 32 mm | No. | 1 | 16500 | 1500 | 18000
2.6 | Auto Air Vent Valves
Make: Anergy / Flamco
Providing and fitting Auto Vent Valves.
a | SITC of Auto air vent in each risers & common headers & AHU. 3/4" auto vent valves at each coil / riser/ header. | Nos. | 2 | 3200 | 500 | 7400
2.7 | SITC of Pressure gauges & Thermometers
Make: H Guru / Waree
Necessary pressure gauges and thermometers 4" Dial type.
a | Water Pressure gauges 150mm dial complete with gauge valves, mounting, fittings and copper tubing extension wherever required. Pressure gauges Range 0-10 Kg/CM2 | Nos. | 2 | 7500 | 800 | 16600
b | Thermometers of the mercury in glass stem type and copper separable well complete with guard etc., of industrial grade mounting on water lines. Length 9/12 inches, Thermometer, Range 0-50 deg C | Nos. | 2 | 2200 | 500 | 5400
c | Thermowells | Nos. | 4 | 1400 | 300 | 6800
d | SITC of Brass Test Plug of industrial grade mounting on water | Nos. | RO
2.8 | INSULATED CONDENSATE DRAIN PIPE
SITC of UPVC pipes of following sizes for drain with necessary supports and fittings such as elbows, tees & reducers etc. The insulation line to be insulated with nitrile rubber insulation of thickness 9mm and wrapped by weather proof protection tape. The Pipe wherever concealed should also have a parallel line as a standby arrangement in case of block of primary pipe .
Make: Supreme, Prince, Astral
a | Φ 25 mm | Rmt | RO
b | Φ 32 mm | Rmt | 10 | 850 | 250 | 11000
NOTES FOR PIPING:
a | Cover all open pipe ends with muslin cloth during construction
b | Pipe cleaning & chemical treatment as per specs shall be included in the piping cost.
c | Unit rates for all indicated sizes of pipes & valves shall be furnished.
d | Cleaning/Painting of pipe before insulation shall be included in piping cost.
e | The piping support should be as per tender specification and additional supports are to be provided Contractor as decided by Consultant.
f | All the valves shall be insulated with the same material as that of Chilled water pipng and cost of insulation for valves shall be considered.
| SUB-TOTAL |  |  |  |  | 134900
3 | VENTILATION SYSTEM
3.1 | KITCHEN DRY SCRUBBER
SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% & units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
Finishing - Power coated, Dark Blue
Operating voltage - 220 Vac+/-10%, 50 Hz (Single phase)
Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
Particle Size - Collects particles as small as 0.01 microns
Motor - Sealead ball bearings UL, single phase.
Cell - Ionizing voltage - 12 KVdc
Collector voltage - 6 KVdc
One cell comprising of 9 ionizing wires and 25 collection plates
Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
Pre-filter - Aluminium mesh, washable Dry contact for BMS.
Make: Rydair / Espair
| CFM - 3100 | No. | 1 | 180000 | 20000 | 200000
| SUB-TOTAL |  |  |  |  | 200000
4 | SHEET METAL WORKS:
4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
a | 18 Gauge GI Sheet Metal Duct (Above 2251mm & Plenum) | Sq.mtr | RO
b | 20 Gauge GI Sheet Metal Duct (1501-2250mm) & For Kitchen Works | Sq.mtr | RO
c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 15 | 1350 | 550 | 28500 | 0
d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 75 | 1250 | 550 | 135000
4.2 | EXTRUDED ALUMINIUM CEILING GRILLES
| Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square/rectangular/Linear). The grilles shall be with 15/30/45° deflections as per requirement. The Colour shall be decided and approved by client and architect. | Sq.mtr | 2.5 | 12000 | 4500 | 41250
Make: Cosmos, Air Master & System Air
4.3 | DOOR TRANSFER GRILLE
SITC of Aluminium extruded powder coated Door transfer grills.
| Door transfer grille (Back to Back) | Sq.mtr | 0.5 | 6500 | 2500 | 4500
Make: Cosmos, Air Master & System Air
4.4 | EXTRUDED ALUMINIUM SQUARE AIR DIFFUSER
Supply, Installation, Testing and Balancing of Powder coated aluminium supply air square diffuser complete with removable inner core as per approved shop drawing and specifications. The diffuser shall also be provided with Black painted GI opposed blade damper (OBD) of required sizes. The diffuser shall be suitable for gypsum/grid ceiling. The Colour shall be decided and approved by client and architect.
Make: Cosmos / Ruskin Titus / Air Master
a | SQUARE DIFFUSER FOR GRID CEILING 600X600mm
| Supply Air Diffuser with OBD - Neck Size 225x225mm | Nos. | 1 | 5500 | 1500 | 7000
4.5 | MULTI LEAF VOLUME CONTROL DAMPER
| SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 1 | 14500 | 2500 | 17000
Make: Cosmos, Air Master & System Air
4.6 | OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 0.5 | 12500 | 2500 | 7500
4.7 | CANVAS CONNECTION
SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
a | For AHU | No | 1 | 11500 | 2500 | 14000
b | For Kitchen Ventilation Fan | Nos. | RO
4.8 | CURTAIN TYPE FIRE DAMPER
SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 / 225°F, etc; as per the approved shop drawings and specifications.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Bare fire dampers | Sq.mtr | 0.25 | 11500 | 2500 | 3500
b | Fusible link as per specification UL 555 | No | 1 | 7500 | 2000 | 9500
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
| SUB-TOTAL |  |  |  |  | 267750
5 | THERMAL & ACOUSTIC INSULATION:
5.1 | THERMAL INSULATION
| Supply & fixing of Thermal insulation for supply air duct using 13mm thick class " O " Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 30 | 750 | 250 | 30000
Make: Armaflex & K-flex
5.2 | ACOUSTIC INSULATION
| Supply & fixing acoustic insulation for ducting using Class "1" closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W/(m.K) and density of 140 - 180 kg/m³. | Sq.mtr | 5 | 1200 | 350 | 7750
Make: Armaflex & K-flex
5.3 | THERMAL INSULATION FOR KITCHEN VENTILATION DUCTS
| SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density : 32 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade. | Sq.mtr | 55 | 1150 | 350 | 82500
Make: Armaflex & K-flex
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.
| SUB-TOTAL |  |  |  |  | 120250
6 | ELECTRICAL WORKS:
6.1 | STARTER PANEL
SITC of indoor / outdoor, wall mounting type 3PH, 415VAC MOTOR STARTERS IN CRCA SHEET STEEL ENCLOSURE with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP & BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB/MCCB, Contactor, Bi-metal O/L relay with SPP, ON/OFF Push buttons, on / off / trip indication Lamp, on off push button, & phase indication Lamp. Selection of relay, contractor, MPCB/MCCB etc. as per Type-2 Coordination. Panel shall have provision to connect with BMS.
a | Suitable for 1500 CFM AHU, DOL Starter Panel | No. | 1 | 22000 | 2000 | 24000
6.2 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
a | Suitable Power Cable:
| Suitable for 1500 CFM AHU, DOL Starter Panel | Rmt | 10 | 750 | 150 | 9000
b | Earthing:
| 8 SWG | Rmt | 20 | 80 | 40 | 2400
6.3 | BTU METER
Supply,fixing and testing of inline Btu meter for the flow rate & temperature measurement consisting mainly of following 3 parts
a) Ultrasonic Flow Meter
b) Matched pair of temp sensor
c) Flowcell Sensor
c) BTU Meter - 4 - 20mA DC from flowmeter
Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+/-) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible & shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc
Make: Honeywell / Danfoss / Siemens
a | Dia 32 mm | No. | 1 | 18500 | 2500 | 21000
6.4 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
a | Suitable for 1500 CFM AHU | No. | 1 | 1200 | 400 | 1600
6.5 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm wide x 50mm x 1.6mm Thick | Rmt | 10 | 1500 | 300 | 18000
| SUB-TOTAL |  |  |  |  | 76000
GRAND TOTAL