## Sheet1
A. CIVIL & INTERIOR BOQ-Ahemedabad Airport |  |  |  |  | Area | 600
Task No. |  | Sub Task No. | Name of Item | Description of Item | Unit | Quantity | Rate | Amount | Remark
F |  |  |  | Electrical
| F.1.0 |  |  | VTPN DB
|  | a.1 | 16 Way VTPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (VTPNDB with vertical busbar) with Double door surface/flush mounted comprising of following:- | Each | 0 |  | 0
Incomer :
|  |  |  | 100A , TM based MCCB of 25kA with O/L, S/C & E/F Protection - 01 No |  |  | 42000 | 0
Outgoing :
6/32A SP MCB - 24 Nos
6/32 Amp TP MCB- 8 Nos
With all necessary connections
|  | a.2 | 12 Way VTPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (VTPNDB with vertical busbar) with Double door surface/flush mounted comprising of following:- | Each | 0 |  | 0
Incomer :
|  |  |  | 63A , TM based MCCB of 25kA with O/L, S/C & E/F Protection - 01 No |  |  | 38000 | 0
Outgoing :
6/32A SP MCB - 18 Nos
6/32 Amp TP MCB- 6 Nos
With all necessary connections
| F.1.0 |  |  | TPN DB |  |  |  | 0
|  | a.1 |  | 125A Manual Changeover Switch | Each | 1
125A 4 Pole Change Over Switch with 125A 4 Pole Isolator input to Main LT Panel in MS enclosure
With all necessary connections
|  | a.1 |  | Main LT Panel - To be read in conjunction with the SLD
14/16 SWG CRCA SHEET STEEL. BASE FRAME SHALL BE MIN. 3.0mm THICK.
Incomer :
100A TP+NL, TM based MCB of 25kA with O/L, S/C & E/F Protection - 01 No
Outgoing : With contactors as indicated in the SLD
63A,TP MCB- 5 Nos
32A,TP MCB- 2 Nos
25A,TPN MCB-1 Nos
|  |  |  | 16A,TP MCB- 4 Nos |  |  | 125000 | 125000
10A SP MCB - 14 Nos
16A SP MCB - 6 Nos
20A SP MCB - 6 Nos
32A TP MCB - 2 Nos
63A FP MCB - 1 Nos.
40A DP MCB - 1 Nos.
32A DP MCB - 9 Nos
25A SP MCB - 12 Nos
32A SP MCB - 2 Nos
Capacitor Bank 3 x 5kVAr + 1 x 3kVAr + 1 x 2kVAr +1 x 1kVAr with all required MCBs,Contactor and accessories
With all necessary connections
|  | a.3 | 8 Way VTPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (VTPNDB with vertical busbar) with Double door surface/flush mounted comprising of following:- | Each | 0 |  | 0
Incomer :
|  |  |  | 63A , TM based MCCB of 25kA with O/L, S/C & E/F Protection - 01 No |  |  | 35000 | 0
Outgoing :
6/32A SP MCB - 12 Nos
6/32 Amp TP MCB- 4 Nos
With all necessary connections
Sub Total of F.1.0 | [7 empty] | 125000
| F.2.0 |  |  | TPN DB
|  | b.1 | 12 Way TPN DB - Kitchen Equipment+ Lighting+Power DB | DB shall have separate neutral links of rating not less than 100A for each phase. The main incoming neutral link shall be in addition to three outgoing neutral links and shall be of 125A. | Each | 0 |  | 0
Incomer :
63A FP, MCB of 10kA - 01 No
|  |  |  | Sub Incomer |  |  | 32000 | 0
3Nos, DP, 63A, RCBO (30mA).
Outgoing :
6/32A SP MCB - 30 Nos
With all necessary connections
|  | b.2 | 8 Way TPN DB - Kitchen Equipment+ Lighting+Power DB | Triple pole and neutral distribution board (TPNDB) with Double door surface/flush mounted of 8 way (4+ 24 Module) 4 Horizontal Rows in 4 Vertical tiers configuration comprising of following:- | Each | 0 |  | 0
DB shall have separate neutral links of rating not less than 100A for each phase. The main incoming neutral link shall be in addition to three outgoing neutral links and shall be of 125A.
8 Way TPN Double door type DB for Power comprising of following:-
Incomer :
|  |  |  | 40A FP MCB,10kA - 01 No |  |  | 30000 | 0
Sub Incomer
3Nos, DP, 40A, RCBO (30mA).
Outgoing :
6/32A SP MCB - 18 Nos
With all necessary connections
|  | b.3 | 6 way TPN DB | Triple pole and neutral distribution board (TPNDB) with Double door surface/flush mounted of 6 way (4+ 18 Module) 4 Horizontal Rows in 4 Vertical tiers configuration comprising of following:- | Each | 0 |  | 0
DB shall have separate neutral links of rating not less than 100A for each phase. The main incoming neutral link shall be in addition to three outgoing neutral links and shall be of 125A.
8 Way TPN Double door type DB for Power comprising of following:-
Incomer :
|  |  |  | 40A FP MCB,10kA - 01 No |  |  | 28000 | 0
Sub Incomer
3Nos, DP, 40A, RCBO (30mA).
Outgoing :
6/32A SP MCB - 12 Nos
With all necessary connections
Sub Total of F.2.0 | [7 empty] | 0
| F.3.0 |  |  | SPN DB
|  | c.1 | 12 Way SPN DB - UPS DB | 12 Way SPN Double door type DB for Power comprising of following:- | Each | 0 |  | 0
Incomer :
32A DP MCB - 01 No
|  |  |  | Outgoing : |  |  | 15000 | 0
6/32A SP MCB - 12 Nos
16A SP MCB -05 Nos
With all necessary connections
|  | c.2 | 8 Way SPN DB - UPS DB | 8 Way SPN Double door type DB for Power comprising of following:- | Each | 2 |  | 0
Incomer :
25A DP MCB - 01 No
|  |  |  | Outgoing : |  |  | 15000 | 30000
16A SP MCB - 04 Nos
10A SP MCB - 02 Nos
With all necessary connections
|  | c.3 | 6 Way SPN DB - UPS DB | 6 Way SPN Double door type DB for Power comprising of following:- | Each | 0 |  | 0
Incomer :
16A DP MCB - 01 No
|  |  |  | Outgoing : |  |  | 14000 | 0
10A SP MCB - 03 Nos
16A SP MCB - 1 No
With all necessary connections
Sub Total of F.3.0 | [7 empty] | 30000
| F.4.0 |  |  | Isolators /ELCB /RCBO & SWITCH SOCKETS
|  | a.1 |  | Supply , installation, testing comissioning of DP isolator of 25 A | Each | 2 | 2550 | 5100
|  | a.2 |  | Supply , installation, testing comissioning of DP isolator of 32 A | Each | 0 | 2850 | 0
|  | a.3 |  | Supply , installation, testing comissioning of DP isolator of 40 A | Each | 0 | 3200 | 0
|  | a.4 |  | Supply , installation, testing comissioning of DP MCB of 25 A | Each | 2 | 2350 | 4700
|  | a.5 |  | Supply , installation, testing comissioning of DP MCB of 32 A | Each | 0 | 2650 | 0
|  | a.6 |  | Supply , installation, testing comissioning of DP MCB of 40 A | Each | 0 | 3000 | 0
|  | a.7 |  | Supply , installation, testing comissioning of FP ELCB of 25 A, 100mA | Each | 0 |  | 0
|  | a.8 |  | Supply , installation, testing comissioning of FP ELCB of 40 A, 100mA | Each | 1 | 4500 | 4500
|  | a.9 |  | Supply , installation, testing comissioning of FP RCBO of 63 A, 100mA | Each | 0 |  | 0
|  | a.10 |  | Supply, Installation, testing comissioning of 10 amp TPN MCB | Each | 0 |  | 0
|  | a.11 |  | Supply, Installation, testing comissioning of 32 amp TPN MCB | Each | 0 |  | 0
|  | a.12 |  | Supply, Installation, testing comissioning of 40 amp TPN MCB | Each | 0 |  | 0
|  | a.13 |  | Providing and fixing TPN/DP enclosure box for indoor purpose | Each | 0 |  | 0
|  | a.14 |  | Providing and fixing TPN/DP enclosure box (Wheather Proof) for outdoor purposes | Each | 0 |  | 0
|  | a.15 |  | Providing and Fixing 16 amp single phase Industrial socket | Each | 0 |  | 0
|  | a.16 |  | Providing and Fixing 25 amp single phase Industrial socket | Each | 0 |  | 0
|  | a.17 |  | Providing and Fixing 25 amp three phase Industrial socket | Each | 0 |  | 0
|  | b |  | ISOLATOR - (BEFORE SERVO STABILIZER) |  |  |  | 0
|  | b.1 |  | 125A FP, 25kA Thermal Magnetic based MCCB with LSIG Protection with Box (As per the instruction of the Engineer Inchrge) | Each | 0 |  | 0
|  | b.2 |  | 100A FP, 25kA Thermal magneticr based MCCB with LSIG Protection with Box(As per the instruction of the Engineer Inchrge) | Each | 1 | 12500 | 12500
|  | c |  | 6/16 Amp Electrical Top | Each | 0 |  | 0
|  |  |  | Supplying and erecting modular type switch socket 6 / 16 A ISI mark approved make duly erected with modular box ,cover plate, & all wiring connections complete. (Single phase) | Each | 23 | 1250 | 28750
|  |  |  | Supplying and erecting modular type switch socket 6 A ISI mark approved make duly erected with modular box , cover plate & all wiring connections complete. (Single phase) | Each | 47 | 1650 | 77550
|  |  |  | Providing and fixing TPN/DP enclosure box for indoor purpose | Each | 0 |  | 0
|  |  |  | Providing and fixing TPN/DP enclosure box (Wheather Proof) for outdoor purposes | Each | 2 | 5500 | 11000
|  |  |  | Providing and Fixing 16 amp single phase Industrial socket | Each | 0 |  | 0
|  |  |  | Providing and Fixing 25 amp single phase Industrial socket | Each | 3 | 4200 | 12600
|  |  |  | Providing and Fixing 25 amp three phase Industrial socket | Each | 4 | 5500 | 22000
|  |  |  | Providing and Fixing 32 amp three phase Industrial socket | Each | 0 |  | 0
|  |  | Light Point Wiring Specifications | Point wiring shall include FRLS wire with all necessary "MMS PVC CONDUIT", with all fittings , accessories , couplings,collars etc., junction / pull / inspection boxes, wires, supports,bushings lamp holders, ceiling rose, flexible conduit, fan hooks wherever required, modular switch, switch box, Fan electronic regulator & terminations using tinned copper lugs of crimping type with cheisling and scaffolding. The scope of sub mains wiring from Panel to DB are excluded.All wiring should be terminated with coupler & connectors.All lighting fixture wiring shall be carried out for primary point using 1.5sqmm copper stranded & for secondary wiring 1sqmm copper stranded conductor 660/1100V grade PVC insulated wire in "PVC Conduit". Individual junction/inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting. From switch board/DB to first light fitting will be termed as primary point and First fitting to subsequent fitting on the same circuit shall be as termed secondary point. Light point wiring shall excluded submains wiring from Panel to DB. The scope of light point wiring starts after switch board/DB where switching control is directly from DB.
|  | d | Lighting points with PVC conduit | Wiring for the following light points with 2X1.5 sq mm PVC insulated copper conductor 650V grade FRLS wires in concealed or surface mounted 20/25mm dia MMS PVC conduit as required including providing 6 amps flush type PVC moulded switches, cover plate,5 sided 1.2mm thick G.I. Box one module for housing switches and earthing of the fixtures and outlet box with 1.5 mm PVC insulated copper conductor 650V grade green earth wire.(switches-as/approved make)- upto 10 Mt. wire length is inclusive.
|  | d.1 |  | Primary (First) light point controlled by a 6A switch. | Nos | 4 | 2250 | 9000
|  | d.2 |  | Primary (First) light point controlled by a MCB in the DB. | Nos | 19 | 2650 | 50350
|  | d.3 |  | Secondary (Loop) light point looped to first point and so on.(upto 6 mtr) wire length | Nos | 150 | 1650 | 247500
|  | d.4 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 1.5 sq.mm and earth wire 1.5 sqmm FRLS PVC copper wire ,in rigid MMS PVC conduit min.25 mm dia, for light/fan/exhaust point from DB to point including all required accessories,etc as per specification.(If wire length increase above 10 mt mentioned in lighting circuit) | RMT |  |  | 0
|  | d.5 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 2.5 sq.mm and earth wire 2.5 sqmm FRLS PVC copper wire ,in rigid MMS PVC conduit min.20 mm dia,including all required accessories,etc as per specification. | RMT | 100 | 275 | 27500
|  | d.6 |  | Supplying & erecting mains with 2x4 sq.mm and earth wire 2.5 sqmm FRLS PVC copper wire laid with conduit/trunking/inside pole/Bus bars or any other places. | RMT | 200 | 340 | 68000
|  | e | Lighting points with MS conduit | Wiring for the following light points with 2X1.5 sq mm PVC insulated copper conductor 650V grade FRLS wires in concealed or surface mounted 20/25mm dia MS conduit as required including providing 6 amps flush type PVC moulded switches, cover plate,5 sided 1.2mm thick G.I. Box one module for housing switches and earthing of the fixtures and outlet box with 1.5 mm PVC insulated copper conductor 650V grade green earth wire.(switches-as/approved make)- upto 10 Mt. wire length is inclusive.
|  | e.1 |  | Primary (First) light point controlled by a 6A switch. | Nos. | 19 | 2450 | 46550
|  | e.2 |  | Primary (First) light point controlled by a MCB in the DB. | Nos. | 18 | 2850 | 51300
|  | e.3 |  | Secondary (Loop) light point looped to first point and so on.(upto 6 mtr) wire length | Nos. | 16 | 1650 | 26400
|  | e.4 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 1.5 sq.mm and earth wire 1.5 sqmm FRLS PVC copper wire ,in rigid MS conduit min.25 mm dia, for light/fan/exhaust point from DB to point including all required accessories,etc as per specification.(If wire length increase above 10 mt mentioned in lighting circuit) | Rmtr | 0 |  | 0
|  | e.5 |  | Supply, Installation, Testing & Commissioning of mains with 2 X 2.5 sq.mm and earth wire 2.5 sqmm FRLS PVC copper wire ,in rigid MS conduit min.20 mm dia,including all required accessories,etc as per specification. | Rmtr | 0 |  | 0
|  | f |  | Power Point wiring
All switch socket wiring shall be carried out for primary point using 3x2.5 sq mm wire in "PVC Conduit" for connection of 6/16amp socket. Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 10 Mt. wire length is inclusive.
|  | f.1 |  | First Point wiring with 6A,5pin wall socket outlet and controlled by a 6A switch | Nos | 3 | 850 | 2550
|  | f.2 |  | Extra loop point wiring with 6A, 5 pin wall socket outlet and controlled by a 6A switch upto 6 mtr length | Nos | 0 |  | 0
|  | f.3 |  | First Point wiring with 16A,5pin wall socket outlet and controlled by a 16A switch | Nos | 0 |  | 0
|  | f.4 |  | Extra loop point wiring with 16A, 5 pin wall socket outlet and controlled by a 16A switch upto 6 mtr length | Nos | 0 |  | 0
|  | f.5 |  | Additional 6 Amp Switch & socket outlet in G.I. Box on modular cover plate adjoining and looped from the existing point. (Note:-additional means switch socket in modular box and plate adjoining the existing one on the same circuit.) Wire will be paid in Rmt separately | Nos |  |  | 0
|  | g |  | All switch socket wiring shall be carried out for primary point using 3X4 sq mm wire in "PVC Conduit" for connection of 16 amp socket . Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS PVC conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 12 Mt. wire length is inclusive.
|  | g.1 |  | First Point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator. | Nos | 27 | 3650 | 98550
|  | g.2 |  | Extra loop point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator.upto 6 mtr wiring | Nos | 2 | 1450 | 2900
|  | g.3 |  | Additional 16 Amp Switch & socket outlet in G.I. Box on modular cover plate adjoining and looped from the existing point. (Note:-additional means switch socket in modular box and plate adjoining the existing one on the same circuit.) . Wire will be paid in Rmt separately | Nos |  |  | 0
|  | g.4 |  | Supply and Laying of Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core wire in surface/recessed medium class MMS PVC conduit alongwith 2 Nos. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Rmtr | 200 | 375 | 75000
|  | h |  | Power Point wiring(MS conduit)
All switch socket wiring shall be carried out for primary point using 3x2.5 sq mm wire in "MS Conduit" for connection of 6/16amp socket. Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 10 Mt. wire length is inclusive.
|  | h.1 |  | First Point wiring with 6A,5pin wall socket outlet and controlled by a 6A switch | Nos | 0 |  | 0
|  | h.2 |  | Extra loop point wiring with 6A, 5 pin wall socket outlet and controlled by a 6A switch upto 6 mtr length | Nos | 0 |  | 0
|  | h.3 |  | First Point wiring with 16A,5pin wall socket outlet and controlled by a 16A switch | Nos | 0 |  | 0
|  | h.4 |  | Extra loop point wiring with 16A, 5 pin wall socket outlet and controlled by a 16A switch upto 6 mtr length | Nos | 0 |  | 0
|  | i |  | All switch socket wiring shall be carried out for primary point using 3X4 sq mm wire in "MS Conduit" for connection of 16 amp socket . Individual junction/inspection boxes shall be provided for each Power Point for the purpose of looping with cheisling and scaffolding work if required .Inclusive of all G.I. Boxing and wire termination & MMS PVC conduit etc. From DB to first switch socket will be termed as primary point and First socket to subsequent looping on the same circuit shall be as termed secondary point. Power point wiring shall excluded submains wiring from Panel to D.B. The scope of Power point wiring starts after DB where switching control is directly from DB.upto 12 Mt. wire length is inclusive.
|  | i.1 |  | First Point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator. | Nos | 0 |  | 0
|  | i.2 |  | Extra loop point wiring with 16A, 3Pin combined shuttered wall socket outlet and controlled by a 16A one way switch with indicator.upto 6 mtr wiring | Nos | 0 |  | 0
|  | j | Conduiting | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall/floor and making good the same in case of recessed conduit as required.
|  | j.1 |  | 20 mm | Rmtr | 50.0047 | 145 | 7250.6815
|  | j.2 |  | 25 mm | Rmtr | 50.0047 | 155 | 7750.7285
|  | j.3 |  | 32 mm | Rmtr | 0 |  | 0
|  | j.4 |  | 40 mm | Rmtr | 0 |  | 0
|  | j.5 |  | 50 mm | Rmtr | 0 |  | 0
|  | k |  | Supplying and fixing of following sizes of MS conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
|  | k.1 |  | 20 mm | Rmtr | 0 |  | 0
|  | k.2 |  | 25 mm | Rmtr | 60 | 185 | 11100
|  | k.3 |  | 32 mm | Rmtr | 0 |  | 0
|  | k.4 |  | 40 mm | Rmtr | 0 |  | 0
|  | k.5 |  | 50 mm | Rmtr | 0 |  | 0
|  | l |  | Supplying & erecting MMS PVC flexible Conduit 25 mm dia.conforming to I.S. and approved make with required number of couplings, bushes, check nuts etc. | Rmtr | 0 |  | 0
|  | m |  | Supplying & erecting M.S flexible Conduit 25 mm dia.conforming to I.S. and approved make with required number of couplings, bushes, check nuts etc. | Rmtr | 0 |  | 0
|  | n |  | Supplying & erecting PVC flexible Conduit 50 mm dia.conforming to I.S. and approved make with required number of couplings, bushes, check nuts etc. | Rmtr | 9.976 | 125 | 1247
|  | o |  | Supply, Installation, Testing & Commissioning of G.I Conduit 32mm dia with necessary accessories in wall/floor with chiselling appropriately as per specification. | Rmtr | 0 |  | 0
|  | p |  | Supply, Installation, Testing & Commissioning of G.I conduit 25 mm in dia with necessary accessories in RCC work/false ceiling/false flooring as per specification | Rmtr | 0 |  | 0
Sub Total of F.4.0 | [7 empty] | 911648.41
| F.5.0 |  |  | LT CABLES & TERMINATIONS
|  | a | SUPPLY AND LAYING OF THE CABLES | Supply, Errecting, Termination & Commissioning of following sizes of 1.1 KV grade FRLS Armoured/Unarmoured Copper/ Aluminum conductor cables laid over MS supports cable racks/trays or fixing on walls including clamping the cable to supports cable racks or fixing on walls including lugs, double compression gland and joints complete in an approved manner as required .
|  | a.1 |  | 3.5Cx25 Sq.mm AL Arm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 4Cx25 Sq.mm AL Arm. XLPE | Rmtr | 30 | 750 | 22500
|  |  |  | 3.5Cx35 Sq.mm AL Arm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 3.5Cx50 Sq.mm AL Arm. XLPE | Rmtr | 30 | 950 | 28500
|  |  |  | 3.5Cx70 Sq.mm AL Arm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 4Cx4 Sq.mm Cu. Arm. XLPE | Rmtr | 75 | 550 | 41250
|  |  |  | 4Cx4 Sq.mm Cu.Unarm. XLPE | Rmtr | 15 | 650 | 9750
|  |  |  | 4Cx2.5 Sq.mm Cu. Arm. XLPE | Rmtr | 10 | 550 | 5500
|  |  |  | 4Cx10 Sq.mm CU. Arm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 4C x 16 sq.mm copper cable | Rmtr | 0 |  | 0
|  |  |  | 4C x 16 sq.mm Cu Uarm.XLPE | Rmtr | 0 |  | 0
|  |  |  | 4Cx 70 sq.mm copper Arm cable | Rmtr | 0 |  | 0
|  |  |  | 4Cx6 Sq.mm CU. XLPE | Rmtr | 0 |  | 0
|  |  |  | 4Cx6 Sq.mm CU. Arm | Rmtr | 0 |  | 0
|  |  |  | 4Cx10 Sq.mm CU. XLPE | Rmtr | 0 |  | 0
|  |  |  | 4Cx2.5 Sq.mm Cu XLPE | Rmtr | 0 |  | 0
|  |  |  | 5Cx 70 sq.mm copper cable | Rmtr | 0 |  | 0
|  |  |  | 3Cx6 Sq.mm Cu. Arm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 3Cx6 Sq.mm Cu. Unarm. XLPE | Rmtr | 30 | 650 | 19500
|  |  |  | 3Cx4 Sq.mm Cu. Arm. XLPE | Rmtr | 30 | 550 | 16500
|  |  |  | 3Cx4 Sq.mm Cu. Unarm. XLPE | Rmtr | 150 | 350 | 52500
|  |  |  | 3Cx2.5 Sq.mm Cu. Unarm. XLPE | Rmtr | 15 | 275 | 4125
|  |  |  | 3Cx2.5 Sq.mm Cu. arm. | Rmtr | 15 | 450 | 6750
|  |  |  | 2Cx1.5 Sq.mm Cu. Unarm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 2Cx2.5 Sq.mm Cu. Arm. XLPE | Rmtr | 0 |  | 0
|  |  |  | 1Cx35 Sq.mm. Cu Unarm XLPE | Rmtr | 0 |  | 0
|  |  |  | 1Cx16 Sq.mm. Cu Unarm XLPE | Rmtr | 0 |  | 0
|  |  |  | 1Cx10 Sq.mm. Cu Unarm XLPE | Rmtr | 0 |  | 0
|  |  |  | 1Cx6 Sq.mm. Cu Unarm XLPE | Rmtr | 0 |  | 0
|  |  |  | 1Cx4 Sq.mm. Cu Unarm XLPE | Rmtr | 0 |  | 0
|  |  | CABLE TERMINATION | Supplying and making indoor Cable end Termination of following sizes 1.1kV grade LT XLPE insulated, HR PVC sheathed, stranded Aluminum/copper conductor, Armoured/ Unarmoured cables as per IS:7098 part-I including cost of tinned copper / Aluminium heavy duty crimpping lugs, double compression weatherproof glands, insulation tape, Name Plate at Both Ends and all necessary material to complete the termination.
|  | b |  | 2/3/3.5/4 CORES AL. CABLE WITH AL. LUGS
|  | b.1 |  | 35 sq.mm. | Jt | 0 |  | 0
|  | b.2 |  | 50 sq.mm. | Jt | 0 |  | 0
|  | b.3 |  | 70 sq.mm. | Jt | 0 |  | 0
|  | c |  | Multicore Flexible Cables : 1100 Volt Annealed Bare Electrolytic High, Conductivity Copper Conductor Flexible PVC Type 'A' Insulated & PVC ST-1 Sheathed Cables in existing Conduit. Conforming to IS: 694:1990 including Making Both End terminations with copper lugs. | Rmtr | 0 |  | 0
|  | c.1 |  | 3C x 2.5mm2 1100V grade flexible copper conductor sheathed FLRS PVC cable (P, N, IG)- IS 694/1990. | Rmtr | 0 |  | 0
|  | c.2 |  | 3C x 4.0mm2 1100V grade flexible copper conductor sheathed FLRS PVC cable (P, N, IG)- IS 694/1990. | Rmtr | 0 |  | 0
Sub Total of F.5.0 | [7 empty] | 206875
| F.6.0 |  |  | EARTHING (In absence of D.G.Vendor)
|  | a.1 |  | Supply & Laying of 25mmX3mm GI strips with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 100 | 450 | 45000
|  | a.2 |  | Supply & Laying of 25mmX3mm CU strips with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 |  | 0
|  | a.3 |  | 25X4 sqmm Earth Alu.Armd cable(For RoofTop) with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 |  | 0
|  | a.4 |  | 35X4 sqmm Earth Alu.Armd cable(For RoofTop) with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 |  | 0
|  | a.5 |  | 8 SWG GI Earth Wire with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 30 | 40 | 1200
|  | a.6 |  | 8 SWG Cu Wire with necessary G. I. Clamps fixed on wall/cable/ conduit with screws in an approved manner. | Mtrs | 0 |  | 0
|  | a.7 |  | Supply, Installation, Testing & Commissioning of long life, Maintenance Free advance chemical Earthing System with 20 year service warranty with 8 feet Vertical Pipe in pipe GI Not less than 1.5” (40mm) ID and not less than 1.5mm wall thickness, & 20x2mm tape inside, which does not require manual addition of water including earthing chamber (300m x 300mm x 300 deep)with cover. The complete systems supported by SEM-20 STRONG based certified advance soil enhancement material. Including all civil works for pit. UOM - Each. This should be done till upto 3 mtr.(Earth resistance value shall be <1 Ohm) | No.'s | 0 |  | 0
|  | a.8 |  | Supply, Installation, testing and commissioning of earth pits comprising 600x600x 3mm thick G.I. electrode/plate 25 mm dia medium class watering G.I. pipe, G.I. funnel with 20 gauge GI wire mesh, masonary chamber with concrete base, CI manhole cover with frame (300m x 300mm x 300 deep) strip from earth palte to link painted with bitumastic paint, test link joint packing the mixture with salt &charcoal 150 mm all around plate electrode complete as required as per IS:3043..(Earth resistance value shall be <1 Ohm) | No.'s | 0 |  | 0
|  | a.9 |  | 4.0 sq.mm. Cu. Flexible cable | Rmtr | 0 |  | 0
|  | a.10 |  | 6.0 sq.mm. Cu. Flexible cable | Rmtr | 0 |  | 0
|  | a.11 |  | 10 sq.mm. Cu. Flexible cable | Rmtr | 10 | 1050 | 10500
|  | a.12 | D.G Foundation | Generator bedding incl of floor raising with debris (4" to 6" )with necessary brickwork at all sides/ with 1:2:4 cement sand metal morter bed as PCC/ IPS/plaster on vertical edges, complete in all respects | Sqft | 0 |  | 0
Sub Total of F 6.0 | [7 empty] | 56700
| F.7.0 |  |  | Cable Trays
|  | a.1 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 300 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner. Including Paints | Rmtr | 15 | 1750 | 26250
|  | a.2 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non -Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 300 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner Including Paint | Rmtr | 0 |  | 0
|  | a.3 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 200 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 20 | 1450 | 29000
|  | a.4 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non -Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 200 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 |  | 0
|  | a.5 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 100 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 |  | 0
|  | a.6 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non- Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 100 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 |  | 0
|  | a.7 |  | Providing & erecting Hot deeped Galvanised Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 50 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 |  | 0
|  | a.8 | Cable Tray -Non Perforated for Kitchen | Providing & erecting Hot deeped Galvanised Non -Perforated type Cable tray manufactured from 18 swg (1.6 mm thick) GI sheet of 50 mm width & 50 mm height complete with necessary coupler plates & hardware in approved manner.Including Paint | Rmtr | 0 |  | 0
|  | b | Raceway | Provind and laying of 2MM thick GI factory fabricated raceways in partition of the following sizes including providing removable 3 mm thick GI cover knock our holes and fixing accessories complete required including floor supports, bends, access boxes and tap of boxes as per instruction from site supervision. |  |  |  | 0
|  | b.1 |  | 300mm wide x 40mm deep | Rmtr | 10 | 1250 | 12500
|  | b.2 |  | 150mm wide x 40mm deep | Rmtr | 10 | 1150 | 11500
|  | b.3 |  | 100mm wide x 40mm deep | Rmtr |  |  | 0
|  | b.4 |  | 50mm wide x 40mm deep | Rmtr |  |  | 0
Sub Total of F.7.0 | [7 empty] | 79250
| F.8.0 |  |  | Electrical Related Civil work
|  | a.1 |  | Excavation/ Cheselling under floor for laying cables/ conduits in wall or floor as per requirement, complete with finishing etc | Sq.Mtr | 20 | 1500 | 30000
Sub Total of F.8.0 | [7 empty] | 30000
| F.9.0 | a |  | Geyser
|  | a.1 |  | SITC of Digital instant GEYSER ABOVE SINK 3 ltr (Ao Smith or equivalent)instant with required accessories) | No. | 2 | 9500 | 19000
|  | a.2 |  | SITC of Storage Geyser (25 ltr) AO smith or equivalent used above 3 way sink with required accessories | No | 1 | 12500 | 12500
Sub Total of F.9.0 | [7 empty] | 31500
|  |  |  | Total |  |  |  | 1470973.41
|  |  |  | GST 18% |  |  |  | 264775.2138
|  |  |  | Grand Total |  |  |  | 1735748.6238

## MAKE
Approved Make List for Electrical / Instrument works
Sr. No | Item Description | Approved Make
1 | Transformer / CSS | Volt amp/ ABB/ Kirloskar/ CG
2 | VCB /HT Breaker Panel | ABB / L&T /Megavin/ Siemens / Schneider
3 | RMU with Cubicle | ABB / L&T /Megavin/ Siemens / Schneider
4 | CT’s / PT’s | L&T/ Siemens/ AE / Indcoil / Kappa / Ricco / Pragati / Megavin
5 | HT Metering | Huphen
6 | LT panels | ABB/ L&T/ Seimens/ Schneider/ Legrand/ Rettal Urmi Technology/Kulaswaminee or Vendors Shall be CPRI / ERDA Approved)
7 | D.B. | Legrand,Schneider,Siemens
8 | Air circuit Breaker | L&T/ ABB / Legrand/ Schneider/ Seimens
9 | MCB / ELCB / RCCB / ISOLATORS / MCCB /DISTRIBUTION BOARDS | L&T/ ABB / Legrand/ Schneider/ Seimens
10 | Surge Protection Device | L&T/ABB/Legrand.
11 | SFU / Fuse Switch Unit | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
12 | HRC Fuses | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
13 | Capacitor | L & T / Malde/ Epcos/ Trinity
14 | APFC Relay | L & T / GEC / Emercon / Alstom
15 | Contactor / Timer / Starter | L & T / ABB
16 | Relays | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
17 | Timer | L&T/ ABB / Legrand/ Schneider/ Seimens / Crompton
18 | Ammeter / Voltmeter / Power factor meter / Frequency meter / Energy meter | Elmeasure/ ABB/ L&T/ Legrand/ Trinity/ Schnieder
20 | Changeover Switch | L&T/ ABB/ C& S
21 | Rotary Switch / Selector Switch | Siemens / L & T / GE / Kaycee
22 | Lightning Pro. System | ABB/ Synergy / Indelec / Stormaster(LPI)/ JEF
23 | UPS | Eaton/ Emerson/ Socomech
24 | Batteries | Exide / Amaron / Panasonic
25 | HT /LT Cables | Polycab/ RR/ KEI/havells
26 | Cables & Wires | Polycab/ RR/ KEI/havells/panasonic
27 | Fire survival cable | AFW / FR Tek / Ravin / Bontn / Tyco
28 | Cable Glands- Double Compression | Dowels / Bracco / Comet
29 | Cable Jointing | Raychem / M Seal
30 | Copper multi-strand wires | Polycab / KEI / RR /Finolex / Gloster
31 | Lugs | Dowels / Bracco / Comet
32 | Cable Tray & Race Ways (Factory Fabricated)& JB | Indiana/ Legrand/ MK/ Globe / Rico Steel
33 | PVC pipes and accessories | Precision / Avonplast / AKG / Modi / Polycab
34 | GI pipes | Zenith / Tata / Jindal
35 | GI Octagonal Poles | Bajaj / Aster / KL Industries
36 | High mast | Bajaj / Transrail
37 | Switches / Sockets / TV, Telephone Socket, etc. (modular)- | L&T/ Legrand / Indoasian/ Anchor ( Wood/Roma ) / MK (Wrapround) / Crabtree (Anthena)
38 | Fan Regulator | MK /Legrand/MDS (To match with the switch / sockets)
39 | Outdoor Boxes | MK/ Clipsal / Henzel / Hunter / Sintex / National
40 | Thermometers
41 | Indicating Meters
42 | Signal Lamps
43 | Push Buttons
44 | Motor / Motor Used in Air wahser | Siemens/ ABB/ Crompton/
45 | Main Fire Alarm Panel (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Apollo
46 | Smoke / Heat Detectors with Base (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Apollo
47 | Devices & Modules (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Apollo
48 | Ceiling fans | Crompton / Havells/ Bajaj / Anchor / Orient / Usha / Khaitan
49 | Exhaust / Pedestal Fan | Crompton / Bajaj / Anchor / Orient / Usha / Khaitan
50 | Fixture | Philips / Crompton /Bajaj / Wipro / LT/ Sudhir
ELV
51 | Telephone Wire / Cables | Finolex / Tata (Lucent) / ITL / Skytone / Gemscab / Delton / National / L&T / Polycab
52 | Television Coaxial Cable | Polycab/ Finolex / RR /RPG / L&T
53 | Network cable | Digisol / Schneider / Avaya/ Systemec / Finolex / Legrand / Dlink
54 | Telephone Instrument | BPL / Tata / Siemens /Avaya / Beetel
55 | Telephone Tag Box | ITL or any equivalent approved make
56 | Automatic Voltage Corrector | Jindal / GES / Muskaan
57 | Annunciator | Areva/ Minilec / Alan
58 | Terminal Blocks | Connect well/ Elmex / Technoplast
59 | Ethernet switch | Sony / Bosch / AVAYA/ Cisco/ Dlink / DigiSol
60 | Patch Panel | AVAYA/ Siemens / Dlink / DigiSol / Legrand
61 | Rack for patch panel & switches | HCL/ Rittal / President / Valrack / Legrand / Digilink
62 | Occupancy Sensor / Day Light Sensor | Siemens, Legrand
63 | BMS system | Siemens.
64 | Cat 6 UTP wire | Legrand, d-link, amps, polycab
65 | Telephone/data wiring accessories | Legrand, d-link, amps, polycab,
66 | 24 port Patch Panel | D-LINK or any other equivalent make
67 | UTP Patch cord | D-LINK or any other equivalent make
68 | Telephone/ TV/ Network poert (modular)- | Legrand/L&T/systimax or Equivalent
69 | Telephone Wire / Cables | L&T / Polycab/ Finolex/ D-link or equivalent
70 | Television Coaxial Cable | Polycab/ Finolex / RR /RPG / L&T
71 | Network cable | Legrand / Dlink/ Digisol / Schneider / Avaya/ Systemec / Finolex /
72 | EPABX | Panasonic/ Systimax/ Avaya / NEC / LG Aria / Siemens / Alcatel
73 | Telephone Instrument | Panasonic/ Systimax/Avaya / Beetel
74 | Telephone Tag Box | ITL or any equivalent
75 | Terminal Blocks | Connect well/ Elmex / Technoplast
76 | Ethernet switch | Sony / Bosch / AVAYA/ Cisco/ Dlink / DigiSol
77 | Patch Panel | AVAYA/ Siemens / Dlink / DigiSol / Legrand
78 | Rack for patch panel & switches | HCL/ Rittal / President / Valrack / Legrand / Digilink
79 | Cat 6 UTP wire | Legrand, d-link, amps, polycab
80 | Telephone/data wiring accessories | Legrand, d-link, amps, polycab,
81 | Conduit | Panasonic/AKG
CCTV
82 | IP IR Box/Bullet Camera | Bosch / Panasonic/ Sony/ Honey well
83 | IP IR Fixed Dome Camera | Bosch / Panasonic/ Sony/ Honey well
84 | IP PTZ Camera | Bosch / Panasonic/ Sony/ Honey well
85 | Network Video Recorder | Bosch / Panasonic/ Sony/ Honey well
86 | POE layer 2 Switch | CISCO/ D-LINK/ ALLIED TELESIS
87 | UTP networking Cat-6 cable | MOLEX/ DLINK/COMSCOPE
88 | Hard disk | WD/ SEAGATE/ Honey well
89 | 40" LED Monitor, Display Resolution : Full HD | LG/ Samsung / Sony
90 | I.S.I. mark Rigid P.V.C. conduit | Precision
91 | POE injector | CISCO or any other equivalent make
92 | Router | D-LINK or any other equivalent make
Emergency Items
93 | Rechargeable torch | Energizer,prolite
94 | Exit signage | Prolite,philips, bajaj
95 | Main Fire Alarm Panel (UL / FM / LPCB Approved) | Notifier/Edwards/Simplex/Morley/System Sensor/Apollo/Ravel
96 | Smoke / Heat Detectors with Base (UL / FM / LPCB Approved) | Simplex /Notifier/Edwards /Morley/ System Sensor/Apollo/Ravel