## BOQ
A. CIVIL & INTERIOR BOQ-Ahemedabad Airport |  |  |  |  | Area | 600
Task No. |  | Sub Task No. | Name of Item | Description of Item | Unit | Quantity | Rate | Amount | Remark
G |  |  |  | Fire Detection and Alarm System
G.1.0
|  | a.1 |  | Supply, Installation, testing & commissioning of addressable type smoke Detector with floating sensitivity Complete with all accessories like base, base box, etc. to be installed under / above false ceiling, roof and concealed space, etc. complete as required. | No. | 4 | 3200 | 12800
|  | c.1 |  | Supply, Installation, testing & commissioning of addressable type manual call point (break glass type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and written 'In case of fire break glass'. | No. | 1 | 2450 | 2450
|  | d.1 |  | Supply, Installation, testing & commissioning of hoooters (Specification :- 110 cd light & 85 dB with adjustable DB) at different locations complete with all fixing accessories, etc under false ceiling roof, wall etc. complete as required. | No. | 1 | 4800 | 4800
|  |  |  | Supply and Installation of ABC powder type fire extinguisher of 3 Kgs. Capacity as per IS :15683, with initial filling in brand new cylinder with powder coated finish, fitted with Gun metal union, discharge hose, wall mounting bracket etc. complete. | No. | 4 | 6500 | 26000
|  |  |  | Supply and Installation of CO2 type fire extinguisher of 4.5 Kgs. Capacity as per IS :15683, with initial filling in brand new cylinder with powder coated finish, fitted with Gun metal union, discharge hose etc. complete. | No. | 1 | 8500 | 8500
|  |  |  | Supply and Installation of Fire Exit Signage | No. | 2 | 1450 | 2900
|  | e.1 |  | Supplying, erecting, testing and commissioning the addressable type Fire Alarm Control Panel (FACP) with standard accessories complete | Set | 1 | 32500 | 32500
|  | f |  | Supplying and erecting PVC armoured cable 2 core 1.5 sq. mm FRLS copper conductor complete erected on wall / celling as per specification | Mtr. | 80 | 210 | 16800
|  | g |  | Supply installation testing and comissioning of Hood supression system(Ceasefire or equivalent). | No. | 1 | 10000 | 10000
|  |  |  | Total |  |  |  | 116750
|  |  |  | GST 18% |  |  |  | 21015
|  |  |  | Grand Total |  |  |  | 137765

## Fire Fighting
Fire Fighting System
|  |  |  | Description of Item | Unit | Qty | Material Rate | Labour Rate | Total Rate | Amount
[7 empty] | (A) | (B)
| A.1.0 |  |  | Water Tank and Pressure Pump for fire figthing System
|  | a | Pump | Supplying, Installation, Testing and Commissioning of Electric Driven Terrace Pump suitable for auto operation and consisting of following: complete in all respect as required.
Horizontal type, centrifugal end suction type pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal and flow of 900 Ipm at 40Mtr head confirming to IS:1520.
Suitable HP squirrel cage induction motor TEFC type suitable for operation on 415 volts ± 10%, 3 phase 50 Hz. AC with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, confirming to IS:325.
M.S. fabricated Common base frame, flexible coupling, coupling guard, foundation bolts and pressure gauge with butterfly valve etc. Suitable cement concrete foundation duly plastered with anti vibration pads.etc. complete as per manufacturer's design & standards and as per detailed specifications.(including all civil works)
The pump shall include suitable weather proof electrical panal with all type of cables,tray,mcbs etc which ever is required.Take approval of panal design from consultnt/client before installation.
Pump electrical panel automation and integration as per site requirement
Sub Total of A.1.0
| A.2.0 |  |  | (PIPING AND ACCESSORIES)
|  | a |  | SLFTC of MS pipes on surface
Supplying, laying, fixing, testing and commissioning of following sizes (NB) of ISI marked heavy class M.S. pipes including cutting, threading, welding etc. and providing all fittings e.g. elbows, reducers, clamps, hangers, flanges, gaskets, nuts, bolts and washers etc. including painting of pipes and fittings with red paint over a coat of ready mixed primer, both of approved quality and shade including cutting holes and chases in brick or RCC walls/slabs and making good the same etc. complete in all respect as required.
|  | a.5 |  | 50mm dia. | Meter | 3.5 |  |  | 1750 | 6125
|  | a.7 |  | 32mm dia. | Meter | 2.5 |  |  | 1450 | 3625
|  | a.8 |  | 25mm dia. | Meter | 17 |  |  | 1350 | 22950
|  | b |  | SITC of butterfly valves
Supplying, Installation, Testing and Commissioning of butterfly valves of PN 1.6 rating of following sizes with nitrile seat and stainless steel stem with lever/gear operation and cast iron body in powder coated finish for fire fighting application complete in all respects as required.
|  | b.2 |  | 65mm dia | Each | 1 |  |  | 7500 | 7500
|  | c |  | SITC of cast iron flanged Non return valves
Supplying, Installation, Testing and Commissioning of cast iron flanged Non return valves of PN 1.6 rating of following sizes conforming to relevant IS specifications and providing and fixing nuts, bolts, washers, gaskets etc. complete as required.
|  | d |  | SITC of Brass Ball Valves
Supply, installation, testing and commissioning of forged brass ball valves with brass body nickel coated, brass ball, hard chrome plated, suitable for fire fighting complete in all respects.
|  | d.1 |  | 50mm dia. | Each | 1 |  |  | 12500 | 12500
|  | e |  | SITC of Cast iron flanged Y Strainer
Supplying, Installation, Testing and Commissioning of CI body flanged (both ends) type Y strainer with (stainless steel / brass mesh) conforming to relevant IS specifications amended upto date complete including providing and fixing nuts, bolts, washers, gaskets etc. complete as required.
|  | f |  | SITC of Pressure Switches
|  |  |  | Supplying, Installation, Testing and Commissioning of pressure switches suitable for operating with fire hydrant systems for working pressure of 14.0 Kg/cm² including electrical control wiring with suitable copper conductor PVC insulated and sheathed control cable upto control panel, connections etc. complete as required. | Each | 1 |  |  | 4500 | 4500
|  | g |  | SITC of Pressure gauge
|  |  |  | Supply, installation, testing & commissioning of 100 mm dia Bourden type, Stainless Steel dial type pressure gauge including brass isolation valve and pipe having calibration of 0-16 Kg/cm2. | Each | 1 |  |  | 11500 | 11500
|  | h |  | SITC of SS orifice plate
|  |  |  | Supplying, Installation, Testing and Commissioning of Stainless steel orifice plates having 6 mm nominal thickness, upto 200mm outer dia. and internal dia. suitable to reduce pressure to between 3.2 to 3.5 Kg/sq.mm., complete as required. | Each | 1 |  |  | 7500 | 7500
|  | i |  | Vibration Bellow
|  |  |  | Total | [5 empty] | 76200
|  |  |  | GST 18% | [5 empty] | 13716
|  |  |  | Grand Total | [5 empty] | 89916

## FIRE MAKE
LIST OF APPROVED MAKES FOR FIRE FIGHTING
S.NO. | ITEMS | APPROVED LIST
A | FIRE ALARM SYSTEM
1 | SMOKE/HEAT DETECTOR WITH BASES (UL LISTED/ FM APPROVED) | APPOLO / SYSTEM SENSOR / APOLLO / RAVEL/
2 | FIRE ALARM PANEL (UL LISTED/ FM APPROVED) | AGNI / RAVEL
3 | MANUAL CALL POINT / HOOTER / RESPONSE INDICATOR (UL LISTED / FM APPROVED) | Agni or equivalent
4 | CABLE | POLYCAB / FINOLEX / RR KABEEL
5 | FIRE EXTINGUISHERS | MINIMAX / CEASE FIRE
6 | Hood supression system | Ceasefire/Swastik/Anshul