## BOQ
PROJECT : KFC , AHMEDABAD AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
PROJECT : KFC , AHMEDABAD AIRPORT
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part D | Electrical Works
1 | Electrical Control Panel
Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop/manual /Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors /over load relay with built in single phase protection / Time delay relay for delayed automatic start of the motor. All panels should have spare NO/ NC Contacts for BMS applications as required.
1.1.3 | Panel-P01 (Kitchen Ventilation)
(2 x 1.1 KW + 1 x 3.75 KW )
INCOMER
-- | 1 No. incoming 32 Amps TP+N MCB
-- | 1 No. Digital Type voltmeter with selector switch with control MCB
-- | 1 No. Digital Type Ammeter 0-40 A with C.T.'s and selector switch.
-- | 1 Set of RYB indication lamps with control MCB
-- | 1 No. of 40 Amps Aluminium conductor 25kA bus bar duly sleeved as required.
OUTGOING
3 Nos. 16 Amps TPN MCB
1 No. DOL starter for 3.75 KW Motor
2 No. DOL starter for 1.1 KW Motor
3 Nos. of single phase preventor (current based-MPRD2)
3 Nos. Digital Type Ammeter
| Each star-delta/DOL starter consists of current operated MN type over load relay, contactor, push button, ON/OFF indication light | Set | 1 | 120000 | 120000
1.2 | Panel-P06 (Ceiling Suspended AHU-2000 CFM)
(1 x 1.1 KW )
OUTGOING
1 Nos. 16 Amps TPN MCB
1 No. DOL starter for 1.1 KW Motor
1 Nos. of single phase preventor (current based-MPRD2)
1 Nos. Digital Type Ammeter
| Each star-delta/DOL starter consists of current operated MN type over load relay, contactor, push button, ON/OFF indication light | Set | 1 | 25000 | 25000
3 | Cables
3.1 | Supplying, laying, testing and commissioning of XLPE insulated aluminium conductor armored cables of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip/wire of suitable size and hardware as per specifications.
iii. | 3 C x 4 Sq. mm | Mtrs | 100 | 555 | 55500
3.2 | Control & Transmission Wiring
i. | Providing & fixing control cum transmission wiring of 2 core x 1.5 sqmm copper in MS conduits between indoor and out door unit and between indoor units and their remote sensor/controller. | RM | 40 | 125 | 5000
3.3 | Power Cabling
3.3.1 | Indoor Units
i. | Providing and fixing flexible power cable of 3 core x 1.5 sqmm copper between Indoor units and their power points | RM | 10 | 225 | 2250
ii. | Providing and fixing flexible power cable of 3 core x 2.5 sqmm copper between Indoor units and their power points | RM | 10 | 245 | 2450
4 | Earthing
Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043:1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required
i. | 25 mm x 3 mm GI strip | RM | 10 | 350 | 3500
ii. | 8 SWG GI Wire | RM | 10 | 65 | 650
| Sub-Total Part-'D' Rs. |  |  |  | 214350
38583
252933